Technical data of dry Transformer

- Power 630 kV type ТСЗ 630/10

- The nominal voltage of TR is 10/0.4 kV

- The nominal current of TR is 36.4/909 A

- Connection group

- Voltage Regulation                        ПБВ +- 5%

|  | H/V | L/V |
| --- | --- | --- |
| 1 | 10 500 | 400 V |
| 2 | 10 250 |  |
| 3 | 10 000 |  |
| 4 | 9 750 |  |
| 5 | 9 500 |  |

- 6. Frequency 50 Hz

- 7. Short-circuit voltage Uk%-7.07% - permissible difference within +- 10%

- 8. The output of high and low voltage windings should be on the racks

- 9. Outputs of high voltage windings should be placed horizontally in the upper part of the transformer.

- 10. Outputs of low voltage windings should be arranged vertically in the upper part of the transformer and neutral output should be installed above phase outputs.

- 11. The transformer should be enclosed in a protective casing

- Casing dimensions are: 2X2.1X1.05 m

13. The winding of the transformer should preferably be made of copper, but the option of aluminum is also considered. (with thermal insulation)

14. Transformer insulation, lightened (so-called dry) insulation thermal resistance class "В"

15. The transformer must work underground, in a closed space, it must be of moisture-resistant so-called tropical performance.

16. Altitude 1000 m above sea level