Minimum Technical Characteristics for Chlorine Gas Containers -  1 ton drums

Description of the Structure

The chlorine-gas container is a welded device of cylindrical structure. Its main elements are: the container itself with the bottom, base, protective rings, fastener, branch pipe, siphon tubes, valves, valve plugs, protective valve and portable hangers. The container has a base for mounting in an upright position, which is welded to the bottom. The flat branch pipe is welded to the surface; the protective valve is attached to the branch pipe with bolts protecting the valves from damage during transport. The container is fitted with welded hangers for carrying.

The chlorine-gas container should bear an identification number clearly engraved on the wall of the housing, as well as the date of technical inspection, the empty container weight. Valves of a full container should be sealed.

Presence of cankered, inflected, dented, deformed or corroded areas on the container housing is not allowed. The container housing should be painted and bear the factory-manufacturer’s inscriptions (identification number and factory name) on its top.

Chlorine Gas Containers’ preferable Technical specifications and minimum standards

| Directive | 2010/35/HU(TPHD) |
| --- | --- |
| Standards applied to designing and manufacture | EN 14208:2004+ADR |
| Capacity | 800 L. |
| Min/ Max. Operating temperature | -20/+75C0 |
| Desing pressure | 32 bar |
| Hydraulic test pressure | 48bar |
| Pneumotic leak tightness test | 6bar |
| Radiography | EN ISO176336-1; EN ISO10675-1 L2 100% |
| Body material type | P265GH |
| PW/HT | 550C0-580C0 -30 min. |
| Dimensions | 2230mm x 770 mm |

Chlorine Gas Containers’ fittings shall be in accordance with the below mentioned Standards:

- Flanges, Washer, Rolling Ring – EN 10025-2;

- Fusible Plug - EN 12165;

- Safety muff – DIN 17100;

- Lifting eyes – EN 10028 2;

- Nut – EN ISO 898-2;

- Bolt - EN ISO 989 -1;

- Valve – EN ISO 10297;

- Valve Protection Cap, Domed ends, Shell – EN 10028-2;

- Gas and Liquid flow pipes – DIN 1629;

Minimum Technical Characteristics for Chlorine Gas Cylinders

The condition of the cylinders must comply with the requirements of the BS EN ISO 9809-1:2019 standard and the resolutions No. 151 and No. 150 of the Government of Georgia dated June 19, 2013.