# MSSP Report

# 1. Project Information

# 2. Overall Material List

## 2.1Equipment List

| Model | Quantity | Description |
| --- | --- | --- |
| MV6-i560WV2GN1 | 1 | V6-i VRF (380-415V) |
| MV6-i450WV2GN1 | 3 | V6-i VRF (380-415V) |
| MDV-D71T2/N1-DA5(B) | 2 | Medium Static Pressure Duct |
| MDV-D56T2/N1-DA5(B) | 9 | Medium Static Pressure Duct |
| MDV-D45T2/N1-DA5(B) | 1 | Medium Static Pressure Duct |
| MDV-D36T2/N1-DA5(B) | 3 | Medium Static Pressure Duct |
| MDV-D28T2/N1-DA5(B) | 20 | Medium Static Pressure Duct |
| MDV-D22T2/N1-DA5(B) | 4 | Medium Static Pressure Duct |
| FQZHN-02D | 16 | Branch joint |
| FQZHN-01D | 16 | Branch joint |
| FQZHN-03D | 4 | Branch joint |
| AHUKZ-03B | 1 | AHU Kit(Standard wired controller KJR-29B) |
| Φ12.7<->Φ15.9 | 4 | Reducer |
| Φ22.2<->Φ25.4 | 1 | Reducer |

## 2.2 Field Providing List

### 2.2.1 Refrigerant Piping Materials

| Model | Quantity | Unit | Description |
| --- | --- | --- | --- |
| Φ6.35 | 80 | m | Copper pipe |
| Φ9.53 | 128 | m | Copper pipe |
| Φ12.7 | 154 | m | Copper pipe |
| Φ15.9 | 145 | m | Copper pipe |
| Φ19.1 | 63 | m | Copper pipe |
| Φ22.2 | 23 | m | Copper pipe |
| Φ25.4 | 5 | m | Copper pipe |
| Φ28.6 | 8 | m | Copper pipe |
| Φ31.8 | 40 | m | Copper pipe |
| Insulation casing for piping |  |  | All refrigerant piping and branch joints should be completely insulated. |

Recommended insulation casing thickness:

| Piping size | Thickness |  |
| --- | --- | --- |
|  | Humidity<80%RH | Humidity≥80%RH |
| Φ6.35~Φ38.1mm | ≥15mm | ≥20mm |
| Φ41.3~Φ38.1mm | ≥20mm | ≥25mm |

### 2.2.2 Refrigerant charge

| System name | Model | Quantity | Unit | Description |
| --- | --- | --- | --- | --- |
| System1 | R410A | 5.27 | kg | Extra Refrigerant Added |
| System2 | R410A | 14.15 | kg | Extra Refrigerant Added |
| System3 | R410A | 5.92 | kg | Extra Refrigerant Added |
| System4 | R410A | 1.1 | kg | Extra Refrigerant Added |
| Total | R410A | 26.44 | kg | Extra Refrigerant Added |

### 2.2.3 Electrical cables

| Type | Size | Length |
| --- | --- | --- |
| Power supply cable | Select based on MCA of each unit | According to the actual system design |
| Communication cable | 0.75mm2 3-core shielded | According to the actual system design |

# 3. Overall Electrical Characteristics

| Model | Quantity | Power supply | MCA(A) | MFA(A) |
| --- | --- | --- | --- | --- |
| MV6-i560WV2GN1 | 1 | 380-415V-3ph-50/60Hz | 45,90 | 50 |
| MV6-i450WV2GN1 | 3 | 380-415V-3ph-50/60Hz | 33,10 | 40 |
| MDV-D71T2/N1-DA5(B) | 2 | 220-240V-50Hz | 0,31 | 15 |
| MDV-D56T2/N1-DA5(B) | 9 | 220-240V-50Hz | 0,31 | 15 |
| MDV-D45T2/N1-DA5(B) | 1 | 220-240V-50Hz | 1,55 | 15 |
| MDV-D36T2/N1-DA5(B) | 3 | 220-240V-50Hz | 1,80 | 15 |
| MDV-D28T2/N1-DA5(B) | 20 | 220-240V-50Hz | 1,00 | 15 |
| MDV-D22T2/N1-DA5(B) | 4 | 220-240V-50Hz | 1,00 | 15 |

Notes:

1. MCA: Minimum Circuit Amps. MCA is used to select wire size.The value in above table is for one unit.

2. MFA: Maximum Fuse Amps. MFA is used to select overcurrent circuit breakers and residual-current circuit breakers.The value in above table is for one unit.

# 4. System1

## 4.1 BOM List (System1)

| Model | Quantity | Unit | Description |
| --- | --- | --- | --- |
| MV6-i560WV2GN1 | 1 |  | V6-i VRF (380-415V) |
| MDV-D71T2/N1-DA5(B) | 2 |  | Medium Static Pressure Duct |
| MDV-D56T2/N1-DA5(B) | 6 |  | Medium Static Pressure Duct |
| MDV-D45T2/N1-DA5(B) | 1 |  | Medium Static Pressure Duct |
| MDV-D28T2/N1-DA5(B) | 1 |  | Medium Static Pressure Duct |
| FQZHN-02D | 1 |  | Branch joint |
| FQZHN-01D | 6 |  | Branch joint |
| FQZHN-03D | 2 |  | Branch joint |
| R410A | 5.27 | kg | Extra Refrigerant Added |
| Φ6.35 | 7 | m | Copper pipe |
| Φ9.53 | 67 | m | Copper pipe |
| Φ12.7 | 8 | m | Copper pipe |
| Φ15.9 | 61 | m | Copper pipe |
| Φ19.1 | 10 | m | Copper pipe |
| Φ22.2 | 1 | m | Copper pipe |
| Φ28.6 | 6 | m | Copper pipe |

## 4.2 Indoor Unit Details (System1)

### 4.2.1 Indoor Unit Details Table

| IDU Name | Model | Weight(kg) | Dimension(WxHxD)(mm) | Power supply | MCA(A) | MFA(A) |
| --- | --- | --- | --- | --- | --- | --- |
| 9 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 10 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 16 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 15 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 12 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 8 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 7 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 4 | MDV-D45T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 1,55 | 15 |
| 6 | MDV-D71T2/N1-DA5(B) | 27.5 | 1218*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 5 | MDV-D71T2/N1-DA5(B) | 27.5 | 1218*210*500 | 220-240V-50Hz | 0,31 | 15 |

| IDU Name | Model | Tmp-C(℃) | RTC(kW) | ATC(kW) | RSC(kW) | ASC(kW) | PI-C(W) | Tmp-H(℃) | RHC(kW) | AHC(kW) | PI-H(W) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,59 |  | 4,59 | 103 | 21 |  | 5,44 | 103 |
| 10 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,54 |  | 4,55 | 103 | 21 |  | 5,44 | 103 |
| 16 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,56 |  | 4,57 | 103 | 21 |  | 5,44 | 103 |
| 15 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,6 |  | 4,6 | 103 | 21 |  | 5,44 | 103 |
| 12 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,8 |  | 2,3 | 57 | 21 |  | 2,81 | 57 |
| 8 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,59 |  | 4,59 | 103 | 21 |  | 5,44 | 103 |
| 7 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,54 |  | 4,55 | 103 | 21 |  | 5,44 | 103 |
| 4 | MDV-D45T2/N1-DA5(B) | 26,0/19,0 |  | 4,5 |  | 3,7 | 98 | 21 |  | 4,32 | 98 |
| 6 | MDV-D71T2/N1-DA5(B) | 26,0/19,0 |  | 7,01 |  | 5,73 | 140 | 21 |  | 6,95 | 140 |
| 5 | MDV-D71T2/N1-DA5(B) | 26,0/19,0 |  | 6,98 |  | 5,7 | 140 | 21 |  | 6,95 | 140 |

| IDU Name | Model | Airflow(m^3/h) | Sound-Pr dB(A) | ESP(Pa) |
| --- | --- | --- | --- | --- |
| 9 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 10 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 16 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 15 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 12 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 8 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 7 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 4 | MDV-D45T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 6 | MDV-D71T2/N1-DA5(B) | 985[H] | 36[H] | 10(0~30) |
| 5 | MDV-D71T2/N1-DA5(B) | 985[H] | 36[H] | 10(0~30) |

| IDU Name | Model | Piping Length to 1st Y Joint(m) |
| --- | --- | --- |
| 9 | MDV-D56T2/N1-DA5(B) | 11,50 |
| 10 | MDV-D56T2/N1-DA5(B) | 17,00 |
| 16 | MDV-D56T2/N1-DA5(B) | 15,00 |
| 15 | MDV-D56T2/N1-DA5(B) | 4,50 |
| 12 | MDV-D28T2/N1-DA5(B) | 9,50 |
| 8 | MDV-D56T2/N1-DA5(B) | 13,00 |
| 7 | MDV-D56T2/N1-DA5(B) | 18,00 |
| 4 | MDV-D45T2/N1-DA5(B) | 11,50 |
| 6 | MDV-D71T2/N1-DA5(B) | 19,00 |
| 5 | MDV-D71T2/N1-DA5(B) | 22,00 |

### 4.2.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Indoor temperature in cooling (Dry bulb temp. / Wet bulb temp. / RH) |
| RTC | Required total cooling capacity |
| ATC | Available total cooling capacity |
| RSC | Required sensible cooling capacity |
| ASC | Available sensible cooling capacity |
| Tmp-H | Indoor temperature in heating (Dry bulb temp.) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| Tdis-H | Indoor unit discharge air temperature in heating |
| Airflow | Indoor unit airflow (High/Medium/Low) |
| ESP | External static pressure |
| Sound-Pr | Sound pressure level (High/Medium/Low) |
| Sound-Po | Sound power level (High/Medium/Low) |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| PI-C | Power input in cooling |
| PI-H | Power input in heating |
| Power supply | Power supply |
| Dimension(WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 4.3 Outdoor Unit Details (System1)

### 4.3.1 Outdoor Unit Details Table

| Model |  | MV6-i560WV2GN1 |
| --- | --- | --- |
| Module |  | MV6-i560WV2GN1 |
| Tmp-C | ℃ | 34.4 |
| RTC | kW |  |
| ATC | kW | 55,09 |
| PI-C | kW | 15,09 |
| EER |  | 3,65 |
| Tmp-H | ℃/℃ | 7,6/6,9 |
| RHC | kW |  |
| AHC | kW | 53,66 |
| PI-H | kW | 12,88 |
| COP |  | 4,16 |
| CR |  | 98,4 |
| Airflow | m^3/h | 17000 |
| Sound-Pr |  | 63 |
| Sound-Po |  |  |
| Bas-Refr | kg | 17,00 |
| Ex-Refr | kg | 5,27 |
| TCO2 eq. |  | 46,50 |
| MCA | A | 45,9 |
| MFA | A | 50 |
| Power supply | V/ph/Hz | 380-415V-3ph-50/60Hz |
| Dimension (WxHxD) | mm | 1340*1635*825 |
| Weight | kg | 344 |

### 4.3.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Outdoor conditions in cooling (Dry bulb temp.) |
| RTC | Required cooling capacity |
| ATC | Available cooling capacity |
| PI-C | Power input in cooling |
| EER | EER |
| Tmp-H | Indoor conditions in heating (Dry bulb temp. / Wet bulb temp. / RH) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| PI-H | Power input in heating |
| COP | COP |
| CR | Combination ratio |
| Airflow | Outdoor unit airflow |
| Sound-Pr | Sound pressure level |
| Sound-Po | Sound power level |
| Bas-Refr | Standard factory refrigerant charge |
| Ex-Refr | Extra refrigerant charge |
| TCO2 eq. | Tonnes of CO2 equivalent |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| Power supply | Power supply |
| Dimension (WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 4.4 Piping Limitations (System1)

### 4.4.1 Piping Limitations

| Item | Capability | Actual Value |
| --- | --- | --- |
| Total piping length | 1000,00(m) | 114,50(m) |
| Longest actual length | 175,00(m) | 25,00(m) |
| Longest equivalent length | 200,00(m) | 27,50(m) |
| Longest equivalent length after first branch | 90,00(m) | 22,00(m) |
| Indoor unit to nearest branch length | 40,00(m) | 8,00(m) |
| Length difference between longest and shortest distance to indoor units | 40,00(m) | 17,50(m) |
| Height difference between indoor and outdoor unit(ODU up) | 90,00(m) | 0,00(m) |
| Height difference between indoor and outdoor unit(ODU down) | 110,00(m) | 0,00(m) |
| Height difference between indoor units | 30,00(m) | 0,00(m) |
| Combination ratio | 50-130% | 98,39% |
| IDU quantity | 33 | 10 |

### 4.4.2 Correction Factors

| Item | Correction factor |
| --- | --- |
| Altitude (indoor unit) | 1,000 |
| Altitude (outdoor unit) | 1,000 |
| Piping (cooling) | 0,988 |
| Piping (heating) | 0,997 |
| Defrost (heating) | 1,000 |

### 4.4.3 Piping Details Table

| No. | Length(m) | Piping diameter |
| --- | --- | --- |
| (1) | 5,00 | Φ28.6/Φ15.9 |
| (2) | 6,00 | Φ19.1/Φ9.53 |
| (3) | 1,00 | Φ28.6/Φ12.7 |
| (4) | 5,00 | Φ15.9/Φ9.53 |
| (5) | 5,00 | Φ15.9/Φ9.53 |
| (6) | 3,00 | Φ15.9/Φ9.53 |
| (7) | 5,00 | Φ15.9/Φ9.53 |
| (8) | 1,00 | Φ22.2/Φ9.53 |
| (9) | 3,00 | Φ15.9/Φ9.53 |
| (10) | 3,00 | Φ15.9/Φ9.53 |
| (11) | 4,00 | Φ19.1/Φ9.53 |
| (12) | 3,00 | Φ15.9/Φ9.53 |
| (13) | 3,00 | Φ12.7/Φ6.35 |
| (14) | 8,00 | Φ15.9/Φ9.53 |
| (15) | 3,00 | Φ15.9/Φ9.53 |
| (16) | 7,00 | Φ15.9/Φ9.53 |
| (17) | 4,00 | Φ12.7/Φ6.35 |
| (18) | 4,00 | Φ15.9/Φ9.53 |
| (19) | 7,00 | Φ15.9/Φ9.53 |

### 4.4.4 Branch Joints Details Table

| No. | Load(kW) | Model |
| --- | --- | --- |
| (1) | 55,1 | FQZHN-03D |
| (2) | 16,8 | FQZHN-01D |
| (3) | 11,2 | FQZHN-01D |
| (4) | 38,3 | FQZHN-03D |
| (5) | 32,7 | FQZHN-02D |
| (6) | 14 | FQZHN-01D |
| (7) | 11,2 | FQZHN-01D |
| (8) | 18,7 | FQZHN-01D |
| (9) | 14,2 | FQZHN-01D |

### 4.4.5 Reducer Details Table

## 4.5 Piping Diagrams (System1)

## 4.6 Wiring Diagrams (System1)

# 5. System2

## 5.1 BOM List (System2)

| Model | Quantity | Unit | Description |
| --- | --- | --- | --- |
| MV6-i450WV2GN1 | 1 |  | V6-i VRF (380-415V) |
| MDV-D36T2/N1-DA5(B) | 2 |  | Medium Static Pressure Duct |
| MDV-D28T2/N1-DA5(B) | 11 |  | Medium Static Pressure Duct |
| MDV-D22T2/N1-DA5(B) | 3 |  | Medium Static Pressure Duct |
| FQZHN-02D | 14 |  | Branch joint |
| FQZHN-03D | 1 |  | Branch joint |
| Φ12.7<->Φ15.9 | 2 |  | Reducer |
| Φ22.2<->Φ25.4 | 1 |  | Reducer |
| R410A | 14.15 | kg | Extra Refrigerant Added |
| Φ6.35 | 42 | m | Copper pipe |
| Φ12.7 | 105 | m | Copper pipe |
| Φ15.9 | 32 | m | Copper pipe |
| Φ19.1 | 39 | m | Copper pipe |
| Φ22.2 | 19 | m | Copper pipe |
| Φ25.4 | 5 | m | Copper pipe |
| Φ31.8 | 32 | m | Copper pipe |

## 5.2 Indoor Unit Details (System2)

### 5.2.1 Indoor Unit Details Table

| IDU Name | Model | Weight(kg) | Dimension(WxHxD)(mm) | Power supply | MCA(A) | MFA(A) |
| --- | --- | --- | --- | --- | --- | --- |
| 22 | MDV-D22T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 23 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 24 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 25 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 26 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 27 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 28 | MDV-D36T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1,8 | 15 |
| 1 | MDV-D22T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 38 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 35 | MDV-D36T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1,8 | 15 |
| 29 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 30 | MDV-D22T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 31 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 32 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 33 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 34 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |

| IDU Name | Model | Tmp-C(℃) | RTC(kW) | ATC(kW) | RSC(kW) | ASC(kW) | PI-C(W) | Tmp-H(℃) | RHC(kW) | AHC(kW) | PI-H(W) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 22 | MDV-D22T2/N1-DA5(B) | 26,0/19,0 |  | 2,09 |  | 1,71 | 57 | 21 |  | 2,14 | 57 |
| 23 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,66 |  | 2,18 | 57 | 21 |  | 2,66 | 57 |
| 24 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,64 |  | 2,17 | 57 | 21 |  | 2,66 | 57 |
| 25 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,62 |  | 2,15 | 57 | 21 |  | 2,66 | 57 |
| 26 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,6 |  | 2,14 | 57 | 21 |  | 2,66 | 57 |
| 27 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,57 |  | 2,11 | 57 | 21 |  | 2,66 | 57 |
| 28 | MDV-D36T2/N1-DA5(B) | 26,0/19,0 |  | 3,27 |  | 2,72 | 61 | 21 |  | 3,26 | 61 |
| 1 | MDV-D22T2/N1-DA5(B) | 26,0/19,0 |  | 2,07 |  | 1,69 | 57 | 21 |  | 2,14 | 57 |
| 38 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,53 |  | 2,08 | 57 | 21 |  | 2,66 | 57 |
| 35 | MDV-D36T2/N1-DA5(B) | 26,0/19,0 |  | 3,39 |  | 2,82 | 61 | 21 |  | 3,26 | 61 |
| 29 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,63 |  | 2,16 | 57 | 21 |  | 2,66 | 57 |
| 30 | MDV-D22T2/N1-DA5(B) | 26,0/19,0 |  | 2,05 |  | 1,68 | 57 | 21 |  | 2,14 | 57 |
| 31 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,6 |  | 2,13 | 57 | 21 |  | 2,66 | 57 |
| 32 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,57 |  | 2,11 | 57 | 21 |  | 2,66 | 57 |
| 33 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,55 |  | 2,1 | 57 | 21 |  | 2,66 | 57 |
| 34 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,52 |  | 2,07 | 57 | 21 |  | 2,66 | 57 |

| IDU Name | Model | Airflow(m^3/h) | Sound-Pr dB(A) | ESP(Pa) |
| --- | --- | --- | --- | --- |
| 22 | MDV-D22T2/N1-DA5(B) | 550[H] | 32[H] | 10(0~30) |
| 23 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 24 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 25 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 26 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 27 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 28 | MDV-D36T2/N1-DA5(B) | 605[H] | 35[H] | 10(0~30) |
| 1 | MDV-D22T2/N1-DA5(B) | 550[H] | 32[H] | 10(0~30) |
| 38 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 35 | MDV-D36T2/N1-DA5(B) | 605[H] | 35[H] | 10(0~30) |
| 29 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 30 | MDV-D22T2/N1-DA5(B) | 550[H] | 32[H] | 10(0~30) |
| 31 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 32 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 33 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 34 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |

| IDU Name | Model | Piping Length to 1st Y Joint(m) |
| --- | --- | --- |
| 22 | MDV-D22T2/N1-DA5(B) | 2,50 |
| 23 | MDV-D28T2/N1-DA5(B) | 9,00 |
| 24 | MDV-D28T2/N1-DA5(B) | 16,00 |
| 25 | MDV-D28T2/N1-DA5(B) | 20,50 |
| 26 | MDV-D28T2/N1-DA5(B) | 25,00 |
| 27 | MDV-D28T2/N1-DA5(B) | 32,50 |
| 28 | MDV-D36T2/N1-DA5(B) | 39,00 |
| 1 | MDV-D22T2/N1-DA5(B) | 16,50 |
| 38 | MDV-D28T2/N1-DA5(B) | 42,00 |
| 35 | MDV-D36T2/N1-DA5(B) | 15,50 |
| 29 | MDV-D28T2/N1-DA5(B) | 16,00 |
| 30 | MDV-D22T2/N1-DA5(B) | 20,50 |
| 31 | MDV-D28T2/N1-DA5(B) | 25,00 |
| 32 | MDV-D28T2/N1-DA5(B) | 31,50 |
| 33 | MDV-D28T2/N1-DA5(B) | 36,00 |
| 34 | MDV-D28T2/N1-DA5(B) | 42,00 |

### 5.2.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Indoor temperature in cooling (Dry bulb temp. / Wet bulb temp. / RH) |
| RTC | Required total cooling capacity |
| ATC | Available total cooling capacity |
| RSC | Required sensible cooling capacity |
| ASC | Available sensible cooling capacity |
| Tmp-H | Indoor temperature in heating (Dry bulb temp.) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| Tdis-H | Indoor unit discharge air temperature in heating |
| Airflow | Indoor unit airflow (High/Medium/Low) |
| ESP | External static pressure |
| Sound-Pr | Sound pressure level (High/Medium/Low) |
| Sound-Po | Sound power level (High/Medium/Low) |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| PI-C | Power input in cooling |
| PI-H | Power input in heating |
| Power supply | Power supply |
| Dimension(WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 5.3 Outdoor Unit Details (System2)

### 5.3.1 Outdoor Unit Details Table

| Model |  | MV6-i450WV2GN1 |
| --- | --- | --- |
| Module |  | MV6-i450WV2GN1 |
| Tmp-C | ℃ | 34.4 |
| RTC | kW |  |
| ATC | kW | 42,3 |
| PI-C | kW | 11,75 |
| EER |  | 3,60 |
| Tmp-H | ℃/℃ | 7,6/6,9 |
| RHC | kW |  |
| AHC | kW | 42,26 |
| PI-H | kW | 9,87 |
| COP |  | 4,28 |
| CR |  | 99,1 |
| Airflow | m^3/h | 13000 |
| Sound-Pr |  | 61 |
| Sound-Po |  |  |
| Bas-Refr | kg | 13,00 |
| Ex-Refr | kg | 14,15 |
| TCO2 eq. |  | 56,69 |
| MCA | A | 33,1 |
| MFA | A | 40 |
| Power supply | V/ph/Hz | 380-415V-3ph-50/60Hz |
| Dimension (WxHxD) | mm | 1340*1635*850 |
| Weight | kg | 277 |

### 5.3.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Outdoor conditions in cooling (Dry bulb temp.) |
| RTC | Required cooling capacity |
| ATC | Available cooling capacity |
| PI-C | Power input in cooling |
| EER | EER |
| Tmp-H | Indoor conditions in heating (Dry bulb temp. / Wet bulb temp. / RH) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| PI-H | Power input in heating |
| COP | COP |
| CR | Combination ratio |
| Airflow | Outdoor unit airflow |
| Sound-Pr | Sound pressure level |
| Sound-Po | Sound power level |
| Bas-Refr | Standard factory refrigerant charge |
| Ex-Refr | Extra refrigerant charge |
| TCO2 eq. | Tonnes of CO2 equivalent |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| Power supply | Power supply |
| Dimension (WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 5.4 Piping Limitations (System2)

### 5.4.1 Piping Limitations

| Item | Capability | Actual Value |
| --- | --- | --- |
| Total piping length | 1000,00(m) | 207,50(m) |
| Longest actual length | 175,00(m) | 71,00(m) |
| Longest equivalent length | 200,00(m) | 74,50(m) |
| Longest equivalent length after first branch | 90,00(m) | 42,00(m) |
| Indoor unit to nearest branch length | 40,00(m) | 7,00(m) |
| Length difference between longest and shortest distance to indoor units | 40,00(m) | 39,50(m) |
| Height difference between indoor and outdoor unit(ODU up) | 90,00(m) | 0,00(m) |
| Height difference between indoor and outdoor unit(ODU down) | 110,00(m) | 0,00(m) |
| Height difference between indoor units | 30,00(m) | 0,00(m) |
| Combination ratio | 50-130% | 99,11% |
| IDU quantity | 26 | 16 |

### 5.4.2 Correction Factors

| Item | Correction factor |
| --- | --- |
| Altitude (indoor unit) | 1,000 |
| Altitude (outdoor unit) | 1,000 |
| Piping (cooling) | 0,943 |
| Piping (heating) | 0,978 |
| Defrost (heating) | 1,000 |

### 5.4.3 Piping Details Table

| No. | Length(m) | Piping diameter |
| --- | --- | --- |
| (1) | 32,00 | Φ31.8/Φ15.9 |
| (2) | 11,00 | Φ22.2/Φ12.7 |
| (3) | 1,00 | Φ25.4/Φ12.7 |
| (4) | 4,00 | Φ25.4/Φ12.7 |
| (5) | 1,00 | Φ12.7/Φ6.35 |
| (6) | 3,00 | Φ22.2/Φ12.7 |
| (7) | 3,00 | Φ12.7/Φ6.35 |
| (8) | 4,00 | Φ19.1/Φ12.7 |
| (9) | 1,00 | Φ12.7/Φ6.35 |
| (10) | 4,00 | Φ19.1/Φ12.7 |
| (11) | 1,00 | Φ12.7/Φ6.35 |
| (12) | 7,00 | Φ19.1/Φ12.7 |
| (13) | 1,00 | Φ12.7/Φ6.35 |
| (14) | 3,00 | Φ19.1/Φ12.7 |
| (15) | 1,00 | Φ12.7/Φ6.35 |
| (16) | 7,00 | Φ12.7/Φ6.35 |
| (17) | 4,00 | Φ12.7/Φ6.35 |
| (18) | 7,00 | Φ12.7/Φ6.35 |
| (19) | 5,00 | Φ22.2/Φ12.7 |
| (20) | 4,00 | Φ12.7/Φ6.35 |
| (21) | 3,00 | Φ19.1/Φ12.7 |
| (22) | 4,00 | Φ19.1/Φ12.7 |
| (23) | 1,00 | Φ12.7/Φ6.35 |
| (24) | 4,00 | Φ19.1/Φ12.7 |
| (25) | 1,00 | Φ12.7/Φ6.35 |
| (26) | 6,00 | Φ19.1/Φ12.7 |
| (27) | 1,00 | Φ12.7/Φ6.35 |
| (28) | 4,00 | Φ19.1/Φ12.7 |
| (29) | 1,00 | Φ12.7/Φ6.35 |
| (30) | 7,00 | Φ12.7/Φ6.35 |
| (31) | 1,00 | Φ12.7/Φ6.35 |

### 5.4.4 Branch Joints Details Table

| No. | Load(kW) | Model |
| --- | --- | --- |
| (1) | 44,6 | FQZHN-03D |
| (2) | 24,8 | FQZHN-02D |
| (3) | 22,6 | FQZHN-02D |
| (4) | 17,6 | FQZHN-02D |
| (5) | 14,8 | FQZHN-02D |
| (6) | 12 | FQZHN-02D |
| (7) | 9,2 | FQZHN-02D |
| (8) | 6,4 | FQZHN-02D |
| (9) | 19,8 | FQZHN-02D |
| (10) | 19,8 | FQZHN-02D |
| (11) | 16,2 | FQZHN-02D |
| (12) | 13,4 | FQZHN-02D |
| (13) | 11,2 | FQZHN-02D |
| (14) | 8,4 | FQZHN-02D |
| (15) | 5,6 | FQZHN-02D |

### 5.4.5 Reducer Details Table

| Reducer Name | Description |
| --- | --- |
| J2-G1 | Φ22.2<->Φ25.4 |
| J8-G1 | Φ12.7<->Φ15.9 |
| J15-G1 | Φ12.7<->Φ15.9 |

## 5.5 Piping Diagrams (System2)

## 5.6 Wiring Diagrams (System2)

# 6. System3

## 6.1 BOM List (System3)

| Model | Quantity | Unit | Description |
| --- | --- | --- | --- |
| MV6-i450WV2GN1 | 1 |  | V6-i VRF (380-415V) |
| MDV-D56T2/N1-DA5(B) | 3 |  | Medium Static Pressure Duct |
| MDV-D36T2/N1-DA5(B) | 1 |  | Medium Static Pressure Duct |
| MDV-D28T2/N1-DA5(B) | 8 |  | Medium Static Pressure Duct |
| MDV-D22T2/N1-DA5(B) | 1 |  | Medium Static Pressure Duct |
| FQZHN-01D | 10 |  | Branch joint |
| FQZHN-02D | 1 |  | Branch joint |
| FQZHN-03D | 1 |  | Branch joint |
| R410A | 5.92 | kg | Extra Refrigerant Added |
| Φ6.35 | 31 | m | Copper pipe |
| Φ9.53 | 61 | m | Copper pipe |
| Φ12.7 | 31 | m | Copper pipe |
| Φ15.9 | 52 | m | Copper pipe |
| Φ19.1 | 14 | m | Copper pipe |
| Φ22.2 | 3 | m | Copper pipe |
| Φ31.8 | 8 | m | Copper pipe |

## 6.2 Indoor Unit Details (System3)

### 6.2.1 Indoor Unit Details Table

| IDU Name | Model | Weight(kg) | Dimension(WxHxD)(mm) | Power supply | MCA(A) | MFA(A) |
| --- | --- | --- | --- | --- | --- | --- |
| 40 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 17 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 39 | MDV-D56T2/N1-DA5(B) | 22 | 997*210*500 | 220-240V-50Hz | 0,31 | 15 |
| 20 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 21 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 42 | MDV-D22T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| IDU1 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 11 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 12 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 13 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 14 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |
| 18 | MDV-D36T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1,8 | 15 |
| 19 | MDV-D28T2/N1-DA5(B) | 17.5 | 778*210*500 | 220-240V-50Hz | 1 | 15 |

| IDU Name | Model | Tmp-C(℃) | RTC(kW) | ATC(kW) | RSC(kW) | ASC(kW) | PI-C(W) | Tmp-H(℃) | RHC(kW) | AHC(kW) | PI-H(W) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 40 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,46 |  | 4,49 | 103 | 21 |  | 5,25 | 103 |
| 17 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,42 |  | 4,45 | 103 | 21 |  | 5,25 | 103 |
| 39 | MDV-D56T2/N1-DA5(B) | 26,0/19,0 |  | 5,36 |  | 4,4 | 103 | 21 |  | 5,25 | 103 |
| 20 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,73 |  | 2,24 | 57 | 21 |  | 2,71 | 57 |
| 21 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,7 |  | 2,22 | 57 | 21 |  | 2,71 | 57 |
| 42 | MDV-D22T2/N1-DA5(B) | 26,0/19,0 |  | 2,09 |  | 1,71 | 57 | 21 |  | 2,18 | 57 |
| IDU1 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,73 |  | 2,24 | 57 | 21 |  | 2,71 | 57 |
| 11 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,7 |  | 2,22 | 57 | 21 |  | 2,71 | 57 |
| 12 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,71 |  | 2,23 | 57 | 21 |  | 2,71 | 57 |
| 13 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,71 |  | 2,23 | 57 | 21 |  | 2,71 | 57 |
| 14 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,68 |  | 2,21 | 57 | 21 |  | 2,71 | 57 |
| 18 | MDV-D36T2/N1-DA5(B) | 26,0/19,0 |  | 3,42 |  | 2,85 | 61 | 21 |  | 3,32 | 61 |
| 19 | MDV-D28T2/N1-DA5(B) | 26,0/19,0 |  | 2,65 |  | 2,18 | 57 | 21 |  | 2,71 | 57 |

| IDU Name | Model | Airflow(m^3/h) | Sound-Pr dB(A) | ESP(Pa) |
| --- | --- | --- | --- | --- |
| 40 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 17 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 39 | MDV-D56T2/N1-DA5(B) | 800[H] | 36[H] | 10(0~30) |
| 20 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 21 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 42 | MDV-D22T2/N1-DA5(B) | 550[H] | 32[H] | 10(0~30) |
| IDU1 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 11 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 12 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 13 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 14 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |
| 18 | MDV-D36T2/N1-DA5(B) | 605[H] | 35[H] | 10(0~30) |
| 19 | MDV-D28T2/N1-DA5(B) | 550[H] | 31[H] | 10(0~30) |

| IDU Name | Model | Piping Length to 1st Y Joint(m) |
| --- | --- | --- |
| 40 | MDV-D56T2/N1-DA5(B) | 10,00 |
| 17 | MDV-D56T2/N1-DA5(B) | 16,50 |
| 39 | MDV-D56T2/N1-DA5(B) | 22,50 |
| 20 | MDV-D28T2/N1-DA5(B) | 12,00 |
| 21 | MDV-D28T2/N1-DA5(B) | 17,50 |
| 42 | MDV-D22T2/N1-DA5(B) | 25,50 |
| IDU1 | MDV-D28T2/N1-DA5(B) | 4,50 |
| 11 | MDV-D28T2/N1-DA5(B) | 18,50 |
| 12 | MDV-D28T2/N1-DA5(B) | 15,50 |
| 13 | MDV-D28T2/N1-DA5(B) | 15,50 |
| 14 | MDV-D28T2/N1-DA5(B) | 22,00 |
| 18 | MDV-D36T2/N1-DA5(B) | 27,50 |
| 19 | MDV-D28T2/N1-DA5(B) | 29,50 |

### 6.2.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Indoor temperature in cooling (Dry bulb temp. / Wet bulb temp. / RH) |
| RTC | Required total cooling capacity |
| ATC | Available total cooling capacity |
| RSC | Required sensible cooling capacity |
| ASC | Available sensible cooling capacity |
| Tmp-H | Indoor temperature in heating (Dry bulb temp.) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| Tdis-H | Indoor unit discharge air temperature in heating |
| Airflow | Indoor unit airflow (High/Medium/Low) |
| ESP | External static pressure |
| Sound-Pr | Sound pressure level (High/Medium/Low) |
| Sound-Po | Sound power level (High/Medium/Low) |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| PI-C | Power input in cooling |
| PI-H | Power input in heating |
| Power supply | Power supply |
| Dimension(WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 6.3 Outdoor Unit Details (System3)

### 6.3.1 Outdoor Unit Details Table

| Model |  | MV6-i450WV2GN1 |
| --- | --- | --- |
| Module |  | MV6-i450WV2GN1 |
| Tmp-C | ℃ | 34.4 |
| RTC | kW |  |
| ATC | kW | 43,89 |
| PI-C | kW | 12,35 |
| EER |  | 3,55 |
| Tmp-H | ℃/℃ | 7,6/6,9 |
| RHC | kW |  |
| AHC | kW | 42,93 |
| PI-H | kW | 10,12 |
| COP |  | 4,24 |
| CR |  | 100,0 |
| Airflow | m^3/h | 13000 |
| Sound-Pr |  | 61 |
| Sound-Po |  |  |
| Bas-Refr | kg | 13,00 |
| Ex-Refr | kg | 5,92 |
| TCO2 eq. |  | 39,50 |
| MCA | A | 33,1 |
| MFA | A | 40 |
| Power supply | V/ph/Hz | 380-415V-3ph-50/60Hz |
| Dimension (WxHxD) | mm | 1340*1635*850 |
| Weight | kg | 277 |

### 6.3.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Outdoor conditions in cooling (Dry bulb temp.) |
| RTC | Required cooling capacity |
| ATC | Available cooling capacity |
| PI-C | Power input in cooling |
| EER | EER |
| Tmp-H | Indoor conditions in heating (Dry bulb temp. / Wet bulb temp. / RH) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| PI-H | Power input in heating |
| COP | COP |
| CR | Combination ratio |
| Airflow | Outdoor unit airflow |
| Sound-Pr | Sound pressure level |
| Sound-Po | Sound power level |
| Bas-Refr | Standard factory refrigerant charge |
| Ex-Refr | Extra refrigerant charge |
| TCO2 eq. | Tonnes of CO2 equivalent |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| Power supply | Power supply |
| Dimension (WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 6.4 Piping Limitations (System3)

### 6.4.1 Piping Limitations

| Item | Capability | Actual Value |
| --- | --- | --- |
| Total piping length | 1000,00(m) | 155,00(m) |
| Longest actual length | 175,00(m) | 35,00(m) |
| Longest equivalent length | 200,00(m) | 38,00(m) |
| Longest equivalent length after first branch | 90,00(m) | 29,50(m) |
| Indoor unit to nearest branch length | 40,00(m) | 10,00(m) |
| Length difference between longest and shortest distance to indoor units | 40,00(m) | 25,00(m) |
| Height difference between indoor and outdoor unit(ODU up) | 90,00(m) | 0,00(m) |
| Height difference between indoor and outdoor unit(ODU down) | 110,00(m) | 0,00(m) |
| Height difference between indoor units | 30,00(m) | 0,00(m) |
| Combination ratio | 50-130% | 100,00% |
| IDU quantity | 26 | 13 |

### 6.4.2 Correction Factors

| Item | Correction factor |
| --- | --- |
| Altitude (indoor unit) | 1,000 |
| Altitude (outdoor unit) | 1,000 |
| Piping (cooling) | 0,978 |
| Piping (heating) | 0,993 |
| Defrost (heating) | 1,000 |

### 6.4.3 Piping Details Table

| No. | Length(m) | Piping diameter |
| --- | --- | --- |
| (1) | 8,00 | Φ31.8/Φ15.9 |
| (2) | 3,00 | Φ22.2/Φ9.53 |
| (3) | 2,00 | Φ19.1/Φ9.53 |
| (4) | 4,00 | Φ19.1/Φ9.53 |
| (5) | 6,00 | Φ15.9/Φ9.53 |
| (6) | 6,00 | Φ15.9/Φ9.53 |
| (7) | 2,00 | Φ15.9/Φ9.53 |
| (8) | 8,00 | Φ15.9/Φ9.53 |
| (9) | 2,00 | Φ15.9/Φ9.53 |
| (10) | 5,00 | Φ15.9/Φ9.53 |
| (11) | 2,00 | Φ12.7/Φ6.35 |
| (12) | 10,00 | Φ12.7/Φ6.35 |
| (13) | 2,00 | Φ12.7/Φ6.35 |
| (14) | 8,00 | Φ19.1/Φ9.53 |
| (15) | 2,00 | Φ12.7/Φ6.35 |
| (16) | 3,00 | Φ15.9/Φ9.53 |
| (17) | 3,00 | Φ15.9/Φ9.53 |
| (18) | 1,00 | Φ12.7/Φ6.35 |
| (19) | 4,00 | Φ12.7/Φ6.35 |
| (20) | 6,00 | Φ15.9/Φ9.53 |
| (21) | 1,00 | Φ12.7/Φ6.35 |
| (22) | 3,00 | Φ15.9/Φ9.53 |
| (23) | 1,00 | Φ12.7/Φ6.35 |
| (24) | 5,00 | Φ12.7/Φ6.35 |
| (25) | 3,00 | Φ12.7/Φ6.35 |

### 6.4.4 Branch Joints Details Table

| No. | Load(kW) | Model |
| --- | --- | --- |
| (1) | 45 | FQZHN-03D |
| (2) | 24,6 | FQZHN-02D |
| (3) | 16,8 | FQZHN-01D |
| (4) | 11,2 | FQZHN-01D |
| (5) | 7,8 | FQZHN-01D |
| (6) | 5 | FQZHN-01D |
| (7) | 20,4 | FQZHN-01D |
| (8) | 17,6 | FQZHN-01D |
| (9) | 5,6 | FQZHN-01D |
| (10) | 12 | FQZHN-01D |
| (11) | 9,2 | FQZHN-01D |
| (12) | 6,4 | FQZHN-01D |

### 6.4.5 Reducer Details Table

## 6.5 Piping Diagrams (System3)

## 6.6 Wiring Diagrams (System3)

# 7. System4

## 7.1 BOM List (System4)

| Model | Quantity | Unit | Description |
| --- | --- | --- | --- |
| MV6-i450WV2GN1 | 1 |  | V6-i VRF (380-415V) |
| AHUKZ-03B | 1 |  | AHU Kit(Standard wired controller KJR-29B) |
| Φ12.7<->Φ15.9 | 2 |  | Reducer |
| R410A | 1.1 | kg | Extra Refrigerant Added |
| Φ12.7 | 10 | m | Copper pipe |
| Φ28.6 | 2 | m | Copper pipe |

## 7.2 Indoor Unit Details (System4)

### 7.2.1 Indoor Unit Details Table

### 7.2.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Indoor temperature in cooling (Dry bulb temp. / Wet bulb temp. / RH) |
| RTC | Required total cooling capacity |
| ATC | Available total cooling capacity |
| RSC | Required sensible cooling capacity |
| ASC | Available sensible cooling capacity |
| Tmp-H | Indoor temperature in heating (Dry bulb temp.) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| Tdis-H | Indoor unit discharge air temperature in heating |
| Airflow | Indoor unit airflow (High/Medium/Low) |
| ESP | External static pressure |
| Sound-Pr | Sound pressure level (High/Medium/Low) |
| Sound-Po | Sound power level (High/Medium/Low) |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| PI-C | Power input in cooling |
| PI-H | Power input in heating |
| Power supply | Power supply |
| Dimension(WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 7.3 Outdoor Unit Details (System4)

### 7.3.1 Outdoor Unit Details Table

| Model |  | MV6-i450WV2GN1 |
| --- | --- | --- |
| Module |  | MV6-i450WV2GN1 |
| Tmp-C | ℃ | 34.4 |
| RTC | kW |  |
| ATC | kW | 45 |
| PI-C | kW | 12,66 |
| EER |  | 3,55 |
| Tmp-H | ℃/℃ | 7,6/6,9 |
| RHC | kW |  |
| AHC | kW | 43,28 |
| PI-H | kW | 10,21 |
| COP |  | 4,24 |
| CR |  | 100,0 |
| Airflow | m^3/h | 13000 |
| Sound-Pr |  | 61 |
| Sound-Po |  |  |
| Bas-Refr | kg | 13,00 |
| Ex-Refr | kg | 1,10 |
| TCO2 eq. |  | 29,44 |
| MCA | A | 33,1 |
| MFA | A | 40 |
| Power supply | V/ph/Hz | 380-415V-3ph-50/60Hz |
| Dimension (WxHxD) | mm | 1340*1635*850 |
| Weight | kg | 277 |

### 7.3.2 Table of Abbreviations

| Abbreviation code | Description |
| --- | --- |
| Tmp-C | Outdoor conditions in cooling (Dry bulb temp.) |
| RTC | Required cooling capacity |
| ATC | Available cooling capacity |
| PI-C | Power input in cooling |
| EER | EER |
| Tmp-H | Indoor conditions in heating (Dry bulb temp. / Wet bulb temp. / RH) |
| RHC | Required heating capacity |
| AHC | Available heating capacity |
| PI-H | Power input in heating |
| COP | COP |
| CR | Combination ratio |
| Airflow | Outdoor unit airflow |
| Sound-Pr | Sound pressure level |
| Sound-Po | Sound power level |
| Bas-Refr | Standard factory refrigerant charge |
| Ex-Refr | Extra refrigerant charge |
| TCO2 eq. | Tonnes of CO2 equivalent |
| MCA | Minimum Circuit Amps |
| MFA | Maximum Fuse Amps |
| Power supply | Power supply |
| Dimension (WxHxD) | Net Dimension (WxHxD) mm |
| Weight | Weight |

## 7.4 Piping Limitations (System4)

### 7.4.1 Piping Limitations

| Item | Capability | Actual Value |
| --- | --- | --- |
| Total piping length | 1000,00(m) | 12,50(m) |
| Longest actual length | 175,00(m) | 10,00(m) |
| Longest equivalent length | 200,00(m) | 10,50(m) |
| Longest equivalent length after first branch | 90,00(m) | 4,00(m) |
| Length difference between longest and shortest distance to indoor units | 40,00(m) | 0,00(m) |
| Height difference between indoor and outdoor unit(ODU up) | 90,00(m) | 0,00(m) |
| Height difference between indoor and outdoor unit(ODU down) | 110,00(m) | 0,00(m) |
| Height difference between indoor units | 15,00(m) | 0,00(m) |
| Combination ratio | 50-130% | 100,00% |
| IDU quantity | 26 | 1 |

### 7.4.2 Correction Factors

| Item | Correction factor |
| --- | --- |
| Altitude (indoor unit) | 1,000 |
| Altitude (outdoor unit) | 1,000 |
| Piping (cooling) | 1,000 |
| Piping (heating) | 1,000 |
| Defrost (heating) | 1,000 |

### 7.4.3 Piping Details Table

| No. | Length(m) | Piping diameter |
| --- | --- | --- |
| (1) | 6,00 | Φ/Φ12.7 |
| (2) | 4,00 | Φ/Φ12.7 |
| (3) | 2,00 | Φ28.6/Φ |

### 7.4.4 Branch Joints Details Table

### 7.4.5 Reducer Details Table

| Reducer Name | Description |
| --- | --- |
| J1-L1 | Φ12.7<->Φ15.9 |
| J1-L2 | Φ12.7<->Φ15.9 |

## 7.5 Piping Diagrams (System4)

## 7.6 Wiring Diagrams (System4)

# 8. Centralized Control Solution

## 8.1 Centralized Controller List

The centralized control system of this project is full output regardless of whether the system is selected.