Project: Gardabani WWTP

FLOTTWEG DECANTER X5E-4/454 Xelletor with SP4.12

# List of contents

List of contents	0

Technical description	3

# Technical description

Separation Task:

Dewatering of primary sludge without digestion

Feed rate:   	45 m³/h

Concentration inlet: 	4%

Volatiles content: 	<68%

Dry solid after dewatering:  	25%

Item 1 	Dewatering decanter centrifuge

### 1 off 	FLOTTWEG decanter centrifuge X5E-4/454 Xelletor with SIMP-DRIVE®  SP 4.12

For highest and most efficient possible dewatering of sludge.

Horizontal, cylindrical/conical solid bowl centrifuge in super-deep pond design with open scroll, for the continuous dewatering of sewage sludge.

The clarified liquid phase flows to the cylindrical end of the bowl. The dewatered solids are conveyed to the conical end of the bowl where they are discharged through ports via centrifugal force.

Technical data:

Bowl ID 	570 mm

Diameter/length ratio 	1 : 4  Cone angle 	17.5°

Volume 	approx. 400 ltr.

Length/width/height  	approx. 4100 x 1550 x 1200 mm

Weight 	approx. 5400 kg

Bowl speed 	3250 rpm (variable)

Max. acceleration factor 	≥ 3340 x g

| Differential speed | 0.5 - 10 rpm (variable) |
| --- | --- |
| Nom. scroll torque | 13000 Nm |
| Scroll design | Flottweg Xelletor Lattice structure based open super-deep pond scroll design. Flottweg Xelletor is the latest state of the art design in decanter scroll engineering. The scroll design merges the infeed chamber and pond surface, thus those parts form one unity. Thereby feed flow will be gently applied directly on the pond surface which leads to lower energy and polymer consumption |

### Recuvane® System

Thanks to the special construction of the RECUVANE® system the centrate can be discharged in a specific way allowing to recover kinetic energy. This energy is utilized to support the main drive. This can reduce the consumed power for the main drive motor by 10 to 20% depending on the pond depth and the suspension.

### Materials

| Product wetted | Cast duplex stainless steel 1.4463 |
| --- | --- |
| supporting bowl parts: | with improved grade (equal to SAF 2205) |
| Scroll: | Cast stainless steel |
|  | 1.4408 and 1.4571 / 1.4404 |
|  | (equal to CF-8M and 316 Ti / 316 L ) |
| Other product wetted | stainless steel 1.4571 / 1.4404 or similar |
| component parts: | (equal to 316 Ti / 316 L ) |
| Belt guard: | chrome steel, powder-coated |
| Other, not product wetted component parts: | carbon steel, painted |
| Drive system | Flottweg SIMP-DRIVE® |
| Bowl drive | Electric motor with V-belt drive. Initial and operating speed settings via frequency inverter (Inverter not included in this item – please see item Control panel, if it is part of the offer). |

| Scroll drive Wear Protection | Co-rotating, multi-stage planetary gear with electric motor and V-belt drive. A special coupling step within the gear enables entirely independent operation of the scroll drive from the bowl drive. The gear is easily accessible, and is mounted away from the bearing blocks and the process area. Differential speed and overload cut-out are electronically controlled by scroll torque feedback via an analogue signal from the frequency inverter (Inverter and control not included in this item – please see item Control panel, if it is part of the offer). |
| --- | --- |
| Scroll flight: | The leading edges of the scroll flight are protected with heat applied tungsten carbide spray |
| Bowl inside: | Tack-welded stainless steel strips in longitudinal direction |
| Bowl outside: | Tungsten carbide stripes |
| Solids discharge: | Ports are protected with hard metal wear bushings |
| Solids housing: | Protected with PU-liner |
| Feed area: | Wear reduced acceleration zone due to plunged lattice structure. |

All wear bushings, hard metal wear segments, and wear liners in the solids housing are replaceable on site.

Lubrication

### Automatic central grease lubrication system

The automatic central grease lubrication system supplies grease to both rotor main bearings via a progressive distributor. The lubricant supply is monitored by a sensor on the progressive distributor. The lubricant quantity will be determined by the duration of working intervals. The supply bin has a capacity of 2 kg and is equipped with a level sensor.

The scroll bearings are sealed-for-life.

### Housing

Horizontally segmented housing

Cover sealed with a shaped flexible gasket

### Sealing system

Both shaft ends of the rotor are sealed with labyrinth seals.

Scroll bearings are provided with slide ring seals.

Static seals: NBR

### Sound insulation

The centrifuge is provided with sound insulation.

The rotor cover is double-walled and filled.

### Painting

in accordance with Flottweg specification "Surface protection for Flottweg Decanters" colour RAL 5007 – brilliant blue colour RAL 7011 – iron grey

colour RAL 9006 – white aluminium

Covers

Drive belt guard is designed in accordance with EN guidelines.

### Rotor base

Welded carbon steel design with rubber isolators mounted underneath the rotor base to dampen vibration induced movement.

### Instrumentation

Differential and bowl speed

Main bearing temperature

Vibration

### 1 off 	Electrical drive motor for bowl

Design:  	in accordance with European Guidelines

IEC 60034

Rated output: 	45 kW

Voltage/frequency: 	400 V / 50 Hz

Speed: 	1500 min-1

Enclosure: 	IP 55

Temperature protection: 	3 PTC-thermistor sensors

Starting: 	frequency converter

(not included in this item)

### 1 off 	Electrical drive motor for scroll

Design:  	in accordance with European Guidelines

IEC 60034

Rated output: 	15 kW

Voltage/frequency: 	400 V / 50 Hz

Speed: 	1500 min-1

Enclosure: 	IP 55

Temperature protection: 	3 PTC-thermistor sensors

Starting: 	frequency converter

(not included in this item)

### Tools

Standard tool in tool box for regular service and operation works. Standard mounting/dismantling device (bearing puller)

Lubrication material

Lubrication material for first replacement filling of the offered unit.

Item 2 	Control Panel

1 off 	Module control cabinet

a. 	Basic configuration

### Electrical control cabinet

Dimensions (WxHxD): 	1200 x 1800 x 500 mm

Base height 100mm

Housing: 	Painted carbon steel RAL 7035

Operating voltage: 	400 V / 50 Hz

Control voltage: 	24 VDC / 230 VAC

Power feed: 	TN-C (L1, L2, L3, PE )

Cable entry: 	from below

Protection class: 	IP54

### Building and testing regulations

Electrical equipment: 	DIN EN 60204-1

Low voltage directive: 	2014/35/EU

Electromagn. compatibility directive: 2014/30/EU

### List of components

Control cabinet housing: 	ELDON

Control: 	ET 200SP CPU 1510-F

(Programmcode Siemens TIA)

IO-System: 	SIEMENS ET200SP

Contactors: 	EATON

Emergency stop module: 	PILZ

### Other electrical control cabinet components

Indicator lamps: "control voltage ON" / "fault indication active"

Overspeed monitoring (safety function)

Vibration monitoring (safety function)

Spare connection (230 VAC) for signal horn or flash light

Control differential speed

b. 	Main components

Frequency converter type: ABB ACS 580

### Drives

1x Decanter Bowl-Drive  	 	45  kW

1x Decanter SIMP-Drive  	 	15  kW

1x Solids diverter gate (elektr. mit "AUMA"-Antrieb)  	0,4  kW

### Machine equipment

1x Autom. grease lubrication (Decanter) 	 	0,75  kW

1x SIMP-Drive air cooled

1x Measurement Decanter (Speed monitoring, vibration)

1x Bearing temp. Decanter

### Plant equipment

1x motor-driven valve Feed  	 	24 V

1x motor-driven valve Solids Diverter  24 V

### c. 	Signal exchange

Type: 	Dry contact

Output: 	Common alarm signal

Release product feed

Request solids output

4 programmable contacts

Input: 	Discharge OK

External start

Product feed operation   	 	Fault polymer station   	 	Fault flocculant min.   	 	Release centrate

1 programmable contacts

### d. 	Control cabinet ventilation

To properly cool the control cabinet a filtered fan is installed in

the door. This blows surrounding air directly into the control cabinet.  An appropriately-sized outtake filter is provided to return the heated  air to the surrounding environment.

Temperature range required: 5 - 30 °C

For other temperature ranges or special environmental conditions 	  	(SO4 or H2S pollution, salty atmosphere) a control cabinet ventilation 	  	is not allowed.

### e. 	Remote Access (eWON COSY)

Installation of a Hardware Remote Access. Access to network only with  	permission by customer. An unauthorized access by Flottweg or a third  	party is not possible. The Remote Access can be disconnected at any time  	by an electrical contact (actuated by the Touch Panel).

Access mode: WLAN

- Operator panel  	Touch Panel Line F 12"

Display: 	12'' wide screen (16:9)

Display surface: 	plastics front

Protection class: 	IP65

Surrounding conditions:

Temperature: 	0°C - 40°C

UV-consistent: 	no

ATEX Area 1 / 2: 	no

Extended vibrational resistance: 	no

- Connection to a BUS system  	Available BUS connection: 	Profibus

Communication type: 	64 Byte read and 64 Byte write

The following signals will be provided as read data:

Analog messages (REAL-data): 	Bowl speed

Differential speed

Scroll torque

Power consumption bowl

Bearing temperature

Number of revolutions

Vibration

Emptying times

Energy consumption

Bit messages (BOOL-data): 	Relevant alarms

The following signals will be provided as write data:

Analog messages (REAL-data): 	Bowl speed

Bit messages (BOOL-data): 	Start / Stop Decanter

Deviation from standard signal exchange only after consultation and at 	  	extra costs!

Additional documentation will be provided in the control panel  	Following documentation will be provided in a printed form.

Optionally this documentation can be provided electronically in .pdf format

1 x Wiring diagram and control panel layout

1 x Parts list of all devices

1 x Terminal layout

1 x Parameter lists for configured devices  	1 x Functional description of operator panels  	      if provided by Flottweg

1 x Operating manual

1 x Cable list (as necessary)

### Appendix: General information about the offered cabinet

Environmental requirements (control cabinet):

Temperature: 	Depends upon cabinet cooling

No direct sunlight

Installation: 	Indoor

Limits according to EN 60721-3-3 class 3C2 (chemically-active):

SO2 Sulphur dioxide: 	< 0,37 cm³/ m³ (ppm)

H2S Hydrogen sulfide: 	< 0,36 cm³/ m³ (ppm)

NH3 Ammonia: 	< 4,2 cm³/ m³ (ppm)

NOx Nitrogen oxides: 	< 0,52 cm³/ m³ (ppm)

Limits according to EN 60721-3-3 class 3K3 (climatic):

Low relative humidity: 	0,05

High relative humidity: 	0,85

Low absolute humidity: 	1 g/m³

High absolute humidity: 	25 g/m³

Low barometric pressure: 	70 kPa

High barometric pressure: 	106 kPa

Limits according to EN 60721-3-3 class 3M1 (mechanical):

Displacement: 	0.3 mm (from 2 to 9 Hz)

Acceleration: 	1 m/s² (bei 9 bis 200 Hz)

Notes regarding electromagnetic compatibility (EMC):

The equipment is qualified for use in an industrial environment according to   	EN 61800-3 category C 3.2 CE. It is not intended for  	use in a public low-voltage network that also supplies residential areas.   	residential areas.

High-frequency interference is to be expected if it is used in such a network.   	Additional interference suppression measures may   	be required.

Requirements for the power supply:

Power quality according to DIN EN 61000-2-4

Overvoltage resistance according to DIN VDE0100 Part 443A (Cat. II)

Terminal connections / exemptions:

The main power feed to the control cabinet and the connections  	to the terminals are not included in this offer. Verification and  	acceptance of the electrical installation at the customer site will be  	according to the local regulations and are the responsibility  	of the customer.

Specific requirements, such as remote connection, customer-requested  	devices, stainless steel or fiberglass housing, different paint colors,  	conductor colors and customer review of design, can also be taken into  	account; please contact us for further technical and commercial  	considerations.

Item 3 	Flexible connectors

### 1 off  	Flexible connectors for

- Sludge feed piping

- Centrate discharge piping

Condensate drain

| Item 5 | Packing, freight and insurance |
| --- | --- |
|  | CIP Gardabani – INCOTERMS 2020, ICC. |
| Item 7 | Solids diverter gate |
| 1 off | Solids diverter 8307.1 |
|  | Actuator drive AUMA-Norm SA07.6, 0,4kW (400V/50Hz) |

during flushing procedure and start or slowdown of the centrifuge, liquid may flow over on solids discharge. To avoid recontamination of dry solids, we recommend the use of our solids diverter.

### For further information please see