## Sheet1
[5 empty] | Project Number |  | P1364 | [5 empty] | Notes: |  |  | PFT : Slurry WPR: Process Water WFR: Gland Seal Water
[5 empty] | Project Name |  | RMG Tailings Thickener Engineering
[5 empty] | Customer |  | JSC RMG Copper | [5 empty] | Prepared | LM | 2022-01-28
[5 empty] | Document Number |  | P1364-EA-004a Combined v5 | [5 empty] | Checked | LRU | 2022-05-09
[5 empty] | Document Name |  | MEASURING POINT LIST | [5 empty] | Approved | LRU | 2022-05-09
[5 empty] | Revision |  | J | [5 empty] | Issued | LRU | 2022-05-09
№ | Dep. | TAG1 | TAG2 | TAG3 | Field dev. TAG | Line / Equipment | Principle | Connection to | Calibration | Cal.unit | Measuring zero | Measuring value | Unit | Additional requirements | Enclosure | DN/Process Connection | Material | PN | Process medium | Flow | Temperature | Density | Device type and L =? | Element type | P&ID Number | Mearuring Range | link to datasheet | Price
[20 empty] | m3/h | °C | kg/m3
1 | ZF01- | LIC- | 200 | LT- | ZF01-LT-200 | ZF01-BA003 | Ultrasonic Level Transmitter | Thickener area Cabinets | 0..3,5 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Mounting bracket | AISI 316 / Aluminum / Plastic |  | PFT | - | -25…40 | 1182 |  |  | P1364-PR-014
2 | ST02- | FIQ- | 205 | FT- | ST02-FT-205 | ST02-2005-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 2000 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 400 | PTFE / Hast.C | 10 | PFT | 1417 | -25…40 | 1182 |  |  | P1364-PR-014
3 | ST02- | DI- | 206 | DT- | ST02-DT-206 | ST02-2005-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=400 mm HDPE Pipe, wall thickness - 20mm) |  |  | PFT | 1417 | -25…40 | 1182 |  |  | P1364-PR-014
4 | ST02- | FIQ- | 207 | FT- | ST02-FT-207 | ST02-2050-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 2000 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 400 | PTFE / Hast.C | 10 | PFT | 1417 | -25…40 | 1182 |  |  | P1364-PR-014
5 | ST02- | DI- | 208 | DT- | ST02-DT-208 | ST02-2050-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=400 mm HDPE Pipe, wall thickness - 20mm) |  |  | PFT | 1417 | -25…40 | 1182 |  |  | P1364-PR-014
| ST02- | FIQ- | 209 | FT- | ST02-FT-209 | ST02-2006-WPR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 120 | m3/h | 4...20 mA Hart | IP67 | 100 | PTFE / Hast.C | 10 | WPR | 100 | -25…40 | 1000 |  |  | P1364-PR-014
6 | ST02- | LIC- | 210 | LT- | ST02-LT-210 | ST02-TK-001 | Micro wave radar or Ultrasonic Level Transmitter | Thickener area Cabinets | 0..5 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Mounting bracket | AISI 316 / Aluminum / Plastic |  | PFT | - | -25…40 | 1182 |  |  | P1364-PR-014
7 | ST02- | DIC- | 221 | DT- | ST02-DT-221 | ST02-2008-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=300 mm HDPE Pipe, wall thickness - 20mm) |  |  | PFT | 503 | -25…40 | 1513 |  |  | P1364-PR-014
8 | ST02- | FICQ- | 222 | FT- | ST02-FT-222 | ST02-2008-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 800 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 300 | PTFE / Hast.C | 10 | PFT | 503 | -25…40 | 1513 |  |  | P1364-PR-014
| ST02- | FIQ- | 228 | FT- | ST02-FT-228 | ST02-2060-WPR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 120 | m3/h | 4...20 mA Hart | IP67 | 100 | PTFE / Hast.C | 10 | WPR | 100 | -25…40 | 1000 |  |  | P1364-PR-014
9 | ST02- | LIC- | 230 | LT- | ST02-LT-230 | ST02-TK-003 | Micro wave radar | Thickener area Cabinets | 0..8,0 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Mounting bracket | AISI 316 / Aluminum / Plastic |  | PFT | - | -25…40 | 1513 |  |  | P1364-PR-014
10 | ST02- | DIC- | 231 | DT- | ST02-DT-231 | ST02-2108-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=300 mm HDPE Pipe, wall thickness - 20mm) |  |  | PFT | 503 | -25…40 | 1513 |  |  | P1364-PR-014
11 | ST02- | FICQ- | 232 | FT- | ST02-FT-232 | ST02-2108-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 800 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 300 | PTFE / Hast.C | 10 | PFT | 503 | -25…40 | 1513 |  |  | P1364-PR-014
12 | ST02- | LIC- | 240 | LT- | ST02-LT-240 | ST02-TK002 | Micro wave radar | Thickener area Cabinets | 0..12,5 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Mounting bracket | AISI 316 / Aluminum / Plastic |  | WPR | - | -25…40 | 1000 |  |  | P1364-PR-014
13 | ST02- | PIC- | 245 | PT- | ST02-PT-245 | ST02-2026-WPR | Pressure Transmitter | Thickener area Cabinets |  |  | 0 | 10,0 | bar | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,1% of scale, Hart protocol support, graphic display, for non-hazardous area, 1 cable gland M20*1,5mm, tag plate | IP67 | G1/2" | AISI 316 / Aluminum |  | WPR | - | -25…40 | 1000 |  |  | P1364-PR-014
14 | ST02- | FIQ- | 246 | FT- | ST02-FT-246 | ST02-2027-WPR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 1600 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 400 | PTFE / Hast.C | 10 | WPR | 1221 | -25…40 | 1000 |  |  | P1364-PR-014
15 | ST02- | FIQ- | 247 | FT- | ST02-FT-247 | ST02-2026-WPR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 500 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 200 | PTFE / Hast.C | 10 | WPR |  | -25…40 | 1000 |  |  | P1364-PR-014
16 | ST02- | FICQ- | 248 | FT- | ST02-FT-248 | ST02-2028-WPR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 500 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 200 | PTFE / Hast.C | 10 | WPR | <200 | -25…40 | 1000 |  |  | P1364-PR-014
17 | ST02- | PI- | 250 | PT- | ST02-PT-250 | ST02-2096-WPR | Pressure Transmitter | Thickener area Cabinets |  |  | 0 | 10,0 | bar | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,1% of scale, Hart protocol support, graphic display, for non-hazardous area, 1 cable gland M20*1,5mm, tag plate | IP67 | G1/2" | AISI 316 / Aluminum |  | WPR | - | -25…40 | 1000 |  |  | P1364-PR-014
18 | ST02- | FIQ- | 252 | FT- | ST02-FT-252 | ST02-2096-WPR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 600 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 250 | PTFE / Hast.C | 10 | WPR |  | -25…40 | 1000 |  |  | P1364-PR-014
19 | ST02- | QI- | 257 | QT- | ST02-QT-257 | ST02-2045-WPR | pH transmitter | Thickener area Cabinets |  |  | 0 | 14 |  | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, Hart protocol support, remote display, for non-hazardous area, cable glands M20*1,5mm, tag plate | IP67 | Meas. Vessel | Glass / AISI 316 | 10 | WPR |  | -25…40 | 1000 |  |  | P1364-PR-014
20 | ST02- | LIC- | 270 | LT- | ST02-LT-270 | ST02-TK-004 | Micro wave radar or Ultrasonic Level Transmitter | Thickener area Cabinets | 0..3,9 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Flange Dn100mm | AISI 316 / Aluminum / Plastic |  | WPR | - | -25…40 | 1000 |  |  | P1364-PR-014
21 | ST02- | FIQ- | 271 | FT- | ST02-FT-271 | ST02-2053-WFR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 25 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 65 | PTFE / Hast.C | 10 | WPR | 5 | -25…40 | 1000 |  |  | P1364-PR-014
22 | ST02- | LI- | 272 | LT- | ST02-LT-272 | ST02-PU-007 | Micro wave radar | Thickener area Cabinets | 0..2,0 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Mounting bracket | AISI 316 / Aluminum / Plastic |  | PFT | - | -25…40 | 1400 |  |  | P1364-PR-014
23 | ST02- | LI- | 273 | LT- | ST02-LT-273 | ST02-PU-008 | Micro wave radar | Thickener area Cabinets | 0..2,0 | m | 0 | 100 | % | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, 4-line display, accuracy - no more than ±4 mm,1 cable gland M20*1,5mm, tag plate | IP67 | Mounting bracket | AISI 316 / Aluminum / Plastic |  | PFT | - | -25…40 | 1400 |  |  | P1364-PR-014
24 | ZF01- | FS- | 275 | PS- | ZF01-PS-275 | ZF01-2048-WFR | Thermal Flow Switch | Thickener area Cabinets |  |  | 0 | 300 | l/h | Power supply 24V DC, DPDT output, display, tag plate | IP67 | 32 | AISI 316 / Aluminum / Plastic | 16 | WFR | 200 | -25…40 | 1000 |  |  | P1364-PR-014
25 | ZF01- | FS- | 276 | PS- | ZF01-PS-276 | ZF01-2049-WFR | Thermal Flow Switch | Thickener area Cabinets |  |  | 0 | 300 | l/h | Power supply 24V DC, DPDT output, display, tag plate | IP67 | 32 | AISI 316 / Aluminum / Plastic | 16 | WFR | 200 | -25…40 | 1000 |  |  | P1364-PR-014
26 | ST02- | FIQ- | 279 | FT- | ST02-FT-279 | ST02-2080-WFR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 25 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 65 | PTFE / Hast.C | 40 | WPR | 5 | -25…40 | 1000 |  |  | P1364-PR-014
27 | ST02- | PIC- | 280 | PT- | ST02-PT-280 | ST02-2080-WFR | Pressure Transmitter | Thickener area Cabinets |  |  | 0 | 40 | bar | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,1% of scale, Hart protocol support, graphic display, for non-hazardous area, 1 cable gland M20*1,5mm, tag plate | IP67 | G1/2" | AISI 316 / Aluminum | 40 | WPR | - | -25…40 | 1000 |  |  | P1364-PR-014
28 | ST02- | FISA- | 285 | FT- | ST02-FT-285 | ST02-2082-WFR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014
| ST02- | FISA- | 287 | FT- | ST02-FT-287 | ST02-2083-WFR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014 |  |  | Removed from P&ID
| ST02- | FISA- | 289 | FT- | ST02-FT-289 | ST02-2084-WFR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014 |  |  | Removed from P&ID
| ST02- | FISA- | 291 | FT- | ST02-FT-291 | ST02-2085-WFR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014 |  |  | Removed from P&ID
29 | ST02- | FISA- | 293 | FT- | ST02-FT-293 | ST02-2087-WFR | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014
| ST02- | FISA- | 295 | FT- | ST02-FT-295 | ST02-2088-WFR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014 |  |  | Removed from P&ID
| ST02- | FISA- | 297 | FT- | ST02-FT-297 | ST02-2089-WFR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014 |  |  | Removed from P&ID
| ST02- | FISA- | 299 | FT- | ST02-FT-299 | ST02-2090-WFR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 6 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, integrated display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 32 | PTFE / Hast.C | 40 | WFR | 1,5 (6) | -25…40 | 1000 |  |  | P1364-PR-014 |  |  | Removed from P&ID
30 | ST02- | FIQ- | 303 | FT- | ST02-FT-303 | ST02-2013-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 600 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 250 | PTFE / Hast.C | 10 | PFT | 503 | -25…40 | 1513 |  |  | P1364-PR-014
31 | ST02- | DIC- | 304 | DT- | ST02-DT-304 | ST02-2013-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=250 mm HDPE Pipe, wall thickness - 20mm) | AISI 316 | 10 | PFT |  | -25…40 | 1513 |  |  | P1364-PR-014
32 | ST02- | FIT | 407 | FIT- | ST02-FIT-407 | ST02-20002-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 503 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 300 | PTFE / Hast.C | 25 | PFT | 418 - 503 | -25…40 | 1513 |  |  | P1364-PR-014
33 | ST02- | DIT | 409 | DIT- | ST02-DIT-409 | ST02-20002-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=3000 mm HDPE Pipe, wall thickness - 20mm) | AISI 316 | 25 | PFT | 418 - 503 | -25…40 | 1513 |  |  | P1364-PR-014
34 | ST02- | PIT | 410 | PIT- | ST02-PIT-410 | ST02-20002-PFT | Pressure Transmitter | Thickener area Cabinets |  |  | 0 | 25 | bar | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,1% of scale, Hart protocol support, graphic display, for non-hazardous area, 1 cable gland M20*1,5mm, tag plate | IP67 | 2" NPT diaphragm seal | AISI 316 / Aluminum | 25 | PFT | 418 - 503 | -25…40 | 1513 |  |  | P1364-PR-014
35 | ST02- | FIT | 424 | FIT- | ST02-FIT-424 | ST02-20001-PFT | Magnetic flow transmitter | Thickener area Cabinets |  |  | 0 | 513 | m3/h | Power supply 24V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, body material - stainless steel, liner's material should correspond to measuring medium, 2 cable glands M20*1,5mm, tag plate | IP67 | 300 | PTFE / Hast.C | 25 | PFT | 418 - 503 | -25…40 | 1513 |  |  | P1364-PR-014
36 | ST02- | DIT | 426 | DIT- | ST02-DIT-426 | ST02-20001-PFT | Radiometric density transmitter | Thickener area Cabinets |  |  | 1000 | 2000 | kg/m3 | Power supply 24V DC, 4...20 mA Hart, 2-wire connection, remote display, radiometric source, mounting bracket, tag plate | IP67 | Mounting bracket (Dn=300 mm HDPE Pipe, wall thickness - 20mm) | AISI 316 | 25 | PFT | 418 - 503 | -25…40 | 1513 |  |  | P1364-PR-014
37 | ST02- | PIT | 427 | PIT- | ST02-PIT-427 | ST02-20001-PFT | Pressure Transmitter | Thickener area Cabinets |  |  | 0 | 25 | bar | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,1% of scale, Hart protocol support, graphic display, for non-hazardous area, 1 cable gland M20*1,5mm, tag plate | IP67 | 2" NPT diaphragm seal | AISI 316 / Aluminum | 25 | PFT | 418 - 503 | -25…40 | 1513 |  |  | P1364-PR-014
| ST02- | PIT | 432 | PIT- | ST02-PIT-432 | ST02-20002-PFT | Pressure Transmitter | GSM to Thickener Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 433 | PIT- | ST02-PIT-433 | ST02-20002-PFT | Pressure Transmitter | Flushing Area Cabinet |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 437 | PIT- | ST02-PIT-437 | ST02-20002-PFT | Pressure Transmitter | Flushing Area Cabinet |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 438 | PIT- | ST02-PIT-438 | ST02-20002-PFT | Pressure Transmitter | GSM to Thickener Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 439 | PIT- | ST02-PIT-439 | ST02-20002-PFT | Pressure Transmitter | GSM to Thickener Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 440 | PIT- | ST02-PIT-440 | ST02-20001-PFT | Pressure Transmitter | GSM to Thickener Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 441 | PIT- | ST02-PIT-441 | ST02-20001-PFT | Pressure Transmitter | Flushing Area Cabinet |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 445 | PIT- | ST02-PIT-445 | ST02-20001-PFT | Pressure Transmitter | Flushing Area Cabinet |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 446 | PIT- | ST02-PIT-446 | ST02-20001-PFT | Pressure Transmitter | GSM to Thickener Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | PIT | 447 | PIT- | ST02-PIT-447 | ST02-20001-PFT | Pressure Transmitter | GSM to Thickener Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0003
| ST02- | FIT | 452 | FIT- | ST02-FIT-452 | ST02-60001-PFT | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 400 | m3/h | AI | IP67 | 400 | SS | 16 | PFT | 200 - 400 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | PIT | 453 | PIT- | ST02-PIT-453 | ST02-60001-PFT | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 16 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 16 | PFT | 200 - 400 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | FIT | 463 | FIT- | ST02-FIT-463 | ST02-20001-PFT | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 503 | m3/h | AI | IP67 | 300 | SS | 10 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | LIT | 464 | LIT- | ST02-LIT-464 | ST02-TK-021 | Micro wave radar | Booster Station Cabinets | 0..7,5 | m | 0 | 100 | % | AI | IP67 | 2" NPT Thread | - | - | PFT | - | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | LSH | 465 | LSHH- | ST02-LSHH-465 | ST02-TK-021 | Vibrating fork level switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | PFT | - | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | LSL | 466 | LSLL- | ST02-LSLL-466 | ST02-TK-021 | Vibrating fork level switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | PFT | - | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | LSH | 468 | LSHL- | ST02-LSHL-468 | ST02-TK-021 | Float Level Switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | PFT | - | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | FIT | 483 | FIT- | ST02-FIT-483 | ST02-40002-PFT | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 503 | m3/h | AI | IP67 | 300 | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | DIT | 484 | DIT- | ST02-DIT-484 | ST02-40002-PFT | Radiometric dens transm | Booster Station Cabinets |  |  | 1000 | 1600 | kg/m3 | AI | IP67 | Stainless Steel 2” Pipe-Mounting Bracket | Housing Material: Polyurethane/epoxy Resin Coated Cast Aluminum NEMA 4X | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | PIT | 485 | PIT- | ST02-PIT-485 | ST02-40002-PFT | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | FIT | 497 | FIT- | ST02-FIT-497 | ST02-40001-PFT | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 503 | m3/h | AI | IP67 | 300 | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | DIT | 498 | DIT- | ST02-DIT-498 | ST02-40001-PFT | Radiometric dens transm | Booster Station Cabinets |  |  | 1000 | 1600 | kg/m3 | AI | IP67 | Stainless Steel 2” Pipe-Mounting Bracket | Housing Material: Polyurethane/epoxy Resin Coated Cast Aluminum NEMA 4X | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | PIT | 499 | PIT- | ST02-PIT-499 | ST02-40001-PFT | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0004
| ST02- | FIT | 561 | FIT- | ST02-FIT-561 | ST02-50001-WPR | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 400 | m3/h | AI | IP67 | 400 | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0005
| ST02- | PIT | 562 | PIT- | ST02-PIT-562 | ST02-50001-WPR | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 16 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0005
| ST02- | FIT | 564 | FIT- | ST02-FIT-564 | ST02-50002-WPR | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 400 | m3/h | AI | IP67 | 400 | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0005
| ST02- | PIT | 565 | PIT- | ST02-PIT-565 | ST02-50002-WPR | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 16 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0005
| ST02- | FSL | 569 | FSL- | ST02-FSL-569 | ST02-60001-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 573 | FSL- | ST02-FSL-573 | ST02-60002-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 577 | FSL- | ST02-FSL-577 | ST02-60003-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 581 | FSL- | ST02-FSL-581 | ST02-60004-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 585 | FSL- | ST02-FSL-585 | ST02-60005-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 589 | FSL- | ST02-FSL-589 | ST02-60006-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 593 | FSL- | ST02-FSL-593 | ST02-60007-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FSL | 597 | FSL- | ST02-FSL-597 | ST02-60008-WPR | Flow low switch | Booster Station Cabinets | [5 empty] | DI | IP67 | DN25 NPT Thread | CS | 63 | WPR | 8 l/min (0.48 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0006
| ST02- | FIT | 601 | FIT- | ST02-FIT-601 | - | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 400 | m3/h | AI | IP67 | 400 | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | PIT | 602 | PIT- | ST02-PIT-602 | - | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 16 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 16 | - | 200 - 400 | -25…40 |  |  |  | H353218-TSF02-270-276-0007
| ST02- | LIT | 604 | LIT- | ST02-LIT-604 | ST02-TK-020 | Micro wave radar | Booster Station Cabinets | 0..8,0 | m | 0 | 100 | % | AI | IP67 | 2" NPT Thread | - | - | WPR | - | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | LSH | 605 | LSHH- | ST02-LSHH-605 | ST02-TK-020 | Vibrating fork level switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | WPR | - | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | LSL | 606 | LSLL- | ST02-LSLL-606 | ST02-TK-020 | Vibrating fork level switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | WPR | - | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | PIT | 619 | PIT- | ST02-PIT-619 | - | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 6 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 10 | - | Minimum Flow: 32 l/min (1.92 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | LIT | 620 | LIT- | ST02-LIT-620 | ST02-TK-022 | Guided Wave Radar | Booster Station Cabinets | 0..4,0 | m | 0 | 100 | % | AI | IP67 | 2" NPT Thread | - | - | WPR | - | -25…40 |  |  |  | H353218-TSF02-270-276-0007
| ST02- | FIT | 621 | FIT- | ST02-FIT-621 | - | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 25 | m3/h | AI | IP67 | 65 | SS | 10 | WPR | Minimum Flow: 32 l/min (1.92 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | LSH | 622 | LSHH- | ST02-LSHH-622 | ST02-TK-022 | Vibrating fork level switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | WPR | - | -25…40 |  |  |  | H353218-TSF02-270-276-0007
| ST02- | LSL | 623 | LSLL- | ST02-LSLL-623 | ST02-TK-022 | Vibrating fork level switch | Booster Station Cabinets | [5 empty] | DI | IP67 | Flanged | - | - | WPR | - | -25…40 |  |  |  | H353218-TSF02-270-276-0007
| ST02- | FIT | 629 | FIT- | ST02-FIT-629 | ST02-70003-WPR | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 25 | m3/h | AI | IP67 | 65 | SS | 63 | WPR | 32 l/min (1.92 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | PIT | 630 | PIT- | ST02-PIT-630 | ST02-70003-WPR | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | WPR | 32 l/min (1.92 m³/hr) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | FIT | 633 | FIT- | ST02-FIT-633 | ST02-70001-WPR | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 1000 | m3/h | AI | IP67 | 300 | SS | 10 | WPR | 690 (792) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | PIT | 634 | PIT- | ST02-PIT-634 | ST02-70001-WPR | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 10 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 10 | WPR | 690 (792) | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0007
| ST02- | FIT | 638 | FIT- | ST02-FIT-638 | ST02-80001-PFT | Magn. flow transmitter | Booster Station Cabinets |  |  | 8 | 20 | m3/h | AI | IP67 | 50 | CS | 10 | PFT | 8 (max (10) | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0008
| ST02- | PIT | 639 | PIT- | ST02-PIT-639 | ST02-80001-PFT | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 6 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | CS | 10 | PFT | 8 (max (10) | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0008
| ST02- | FIT | 642 | FIT- | ST02-FIT-642 | ST02-60001-PFT | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 1000 | m3/h | AI | IP67 | 400 | CS | 16 | PFT | 0 - 400 | -25…40 | 1513 |  |  | H353218-TSF02-270-276-0008
| ST02- | FIT | 647 | FIT- | ST02-FIT-647 | ST02-60001-WPR | Magn. flow transmitter | Flushing Area Cabinet |  |  | 0 | 1000 | m3/h | AI | IP67 | 400 | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0003
| ST02- | FIT | 648 | FIT- | ST02-FIT-648 | ST02-60001-WPR | Magn. flow transmitter | Booster Station Cabinets |  |  | 0 | 1000 | m3/h | AI | IP67 | 400 | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0008
| ST02- | FIT | 649 | FIT- | ST02-FIT-649 | ST02-60001-WPR | Magn. flow transmitter | Thickener area Cabinets |  |  | 0 | 1000 | m3/h | AI | IP67 | 400 | SS | 16 | WPR | 200 - 400 | -25…40 | 1000 |  |  | H353218-TSF02-270-276-0003
| ST02- | FIT | 650 | PIT- | ST02-PIT-650 | ST02-20001-PFT | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | -
| ST02- | PIT | 651 | PIT- | ST02-PIT-651 | ST02-20001-PFT | Pressure Transmitter | Booster Station Cabinets |  |  | 0 | 50 | bar | 4-20 mA + Hart | IP67 | 2" NPT diaphragm seal | SS | 63 | PFT | 418 - 503 | -25…40 | 1513 |  |  | -