Polyelectrolyte dosage:

Cationic polyelectrolyte is used for chemical conditioning of this type of sludge.

It is estimated a dose of 8 kg polyelectrolyte/t (average conditions) and 10 kg polyelectrolyte/t

(max. conditions)

The reagent is prepared in three automatic continuous-mode production installations that consists of a vat with three compartments, two of them with agitation. The polyelectrolyte is dosed in powder form by means of a dosage screw that includes a storage hopper of 100 liters.

With each unit a continuous unitary production of 0.5% polyelectrolyte is achieved at 8,000 l/h.

The dosage will be carried out by means of two (1+1) progressive cavity pumps; with a flow of 1,400 - 3,700 l/h and 10 w.c.m. o pressure. All pumps will be equipped with variable frequency converters.

Water is incorporated in the discharge of the dosage pumps to dilute the reagent to 0.2% and the dilution flow is regulated by means of in-line rotameters.

The polyelectrolyte is dosed in the sludge intake pipes to the centrifuges.

POLYELECTROLYTE SOLUTION - PREPARATION AND DOSING

Reagent:

Polyelectrolyte

Doses and Consumption

Dry matter to treat

• By design:                                                                                  1.600,00          kg/h

• Maximum by pumping:                                                            1.800,00          kg/h

Dose

• Average:                                                                                        8,00              kg/tn

• Maximum:                                                                                    10,00             kg/tn

Hourly consumption at maximum load by pumping

• Average:                                                                                       14,40             kg/h

• Maximum:                                                                                    18,00             kg/h

Daily consumption

• Average:                                                                                      204,80            kg/d

• Maximum:                                                                                   256,00            kg/d

Storage of powdered product

Type of supply:

Solid

Commercial product purity:                                                             100              % Density:                                                                                             0,50              kg/l Autonomy of storage by average dose:                                          15,00             d Required capacity:                                                                        3.072,00          kg Adopted capacity:                                                                            3.100             kg

Dilution

Preparation system:

Automatic

Number of installed equipments:                                                       1                ut

Number of equipments on duty:                                                        1                ut

System:

| • Average: | 14,40 | kg/h |
| --- | --- | --- |
| • Maximum: | 18,00 | kg/h |
| Dilution concentration: | 0,50 | % |
| Number of dilution equipments on duty: | 1 | ut |
| Number of compartments for each tank: | 3 | uts |
| Number of dilution mixers per equipment: | 2 | uts |
| Required capacity |  |  |
| • Average dose: | 2.880,00 | l/h |
| • Maximum dose: | 3.600,00 | l/h |
| Adopted capacity: | 8.000 | l/h |
| Volume: | 8.000 | l |
| Maturation time: | 30 | min |

Required capacity

Volumetric dos

Dosing

System:

Progressive cavity pump

Total number of installed pumps:                                                      2                uts Total number of pumps on duty:                                                        1                ut Total number of stand-by pumps:                                                      1                ut Maximum unitary flow demanded:                                             3.600,00          l/h Maximum unitary flow adopted:                                                    3.700             l/h Range of flow adopted:                                                            1.400 - 3.700      l/h

Type of dosage: Range adjustment: Control system:

Post-dilution to dosage "in line":

Automatic proportional to the flow

Automatic  4 ÷ 20 mA signal

Frequency converter

• Secondary dilution concentration in line:                                    0,20              %

• Maximum unitary flow water for dilution:                              5.550             l/h

• Measurement system:

Variable area flowmeter

• Number of installed rotameters:                                                     1                ut

• Number of rotameters on duty:                                                       1                ut

| • Required unitary flow: | 5.550 | l/h |
| --- | --- | --- |
| • Unitary flow adopted: | 500 - 6.300 | l/h |