Request for Proposal (RFP)

Tbilisi Mall Fire Alarm System Rectification Works

- PURPOSE

The purpose of this RFP is to solicit proposals from qualified contractors for the rectification works of the fire alarm system at Tbilisi Mall. The objective is to ensure the replacement of existing control panels, upgrading two software systems to the latest versions, and ensuring proper communication between all fire equipment to avoid malfunctions with other systems, such as jet fans, smoke extractors, emergency door closing systems, and the mall evacuation announcement system.

- SCOPE OF WORK

The contractor will be responsible for:

- Preparation of Layouts for Detectors and Components
Site Survey - Conduct a thorough site survey of all levels of the building to map out the existing placement of fire detectors (including CO, smoke, heat detectors) and related components
Layout Design - Prepare detailed floor layouts for each level, indicating the exact location and type of each detector, alarm, and related fire safety component
Ensure that the layouts comply with local fire safety regulations and industry standards
Approval Process - Submit the layouts for review and approval by the relevant stakeholders before finalizing.

- Preparation of Control Panel Diagrams
Control Panel Mapping - Create detailed diagrams of all fire alarm control panels, indicating which detectors and components are connected to which control panels
Group connections logically based on loops and zones, and indicate the relationship between different panels and the detectors they control
Communication Pathways - Diagram the communication pathways between control panels and connected systems, such as jet fans, smoke extractors, emergency door closing systems, and the mall evacuation announcement system
Panel Integration - Ensure that the diagrams reflect the integration of new and existing systems, highlighting any changes or upgrades required to ensure seamless communication and operation
Documentation - Provide a comprehensive set of documents that include the layouts, control panel diagrams, and explanations of the interconnections and functionality of the system.
Compliance and Standards - Ensure that all diagrams adhere to the latest industry standards and regulations

- Reporting and Updates
Progress Reports - Provide regular progress reports on the development of layouts and diagrams, including any issues or required adjustments
Final Documentation - Submit a final set of approved and detailed layouts and diagrams, along with an explanation of the control panel connections, to be used for ongoing maintenance and future upgrades.

- Coordination and Meetings
Regular Coordination - Coordinate with the project team to ensure that all layouts and diagrams meet the project’s requirements. Attend regular meetings with the project management team to discuss progress, challenges, and any necessary adjustments.

- Quality Assurance
Verification - Verify that all layouts and diagrams are accurate and that all components and connections are correctly represented.
Final Inspection - Conduct a final inspection to ensure that the layouts and control panel diagrams meet the project’s specifications and are ready for implementation.

- Preparing a detailed project plan and providing a Bill of Quantities (BOQ) for the rectification works.

- Replacing existing control panels to ensure the efficient operation of the fire alarm system.

- Replacing any damaged detectors (including CO, smoke, heat detectors) to maintain full system functionality.

- Implementing software upgrades for fire alarm visualization and addressing to bring the system up to date.

- Readdressing all detectors to ensure proper communication between all fire equipment and avoid system malfunctions.

- Providing a detailed report outlining the rectification plan, including any findings and proposed solutions.

- Providing a detailed time schedule of work to ensure timely completion of the rectification works.

- Ensuring compatibility of the new upgrades with existing installations without altering the existing fire alarm detectors and cabling.

- EXISTING SITUATION

The existing FP2000 series fire alarm panels have many errors. These panels are old and are no longer produced. The manufacturer of the FP2000 series fire alarm panels no longer provide technical support or spare parts, necessitating the replacement of all panels with a new series to ensure efficient and stable operation of the system. The number of panels should be determined based on the number of loops available.
* Total Loops: 80 pcs
* Total Addressable Devices 7361
* Old Version Software ATS 8600

Room #1

- 3 pcs FP2000 Fire Alarm Panels

- Total Loops: 22 pcs

- Total Faults: 34 pcs

- 1st FAP: 9 pcs communication faults

- 2nd FAP: 6 pcs communication faults, 16 pcs new devices

- 3rd FAP: 1 pcs communication fault, 2 pcs pollution faults

Room #2

- 2 pcs FP2000 Fire Alarm Panels

- Total Loops: 9 pcs

- Total Faults: 36 pcs

- 4th FAP: No faults

- 5th FAP: 22 pcs communication faults, 4 pcs new devices. 2 pcs pollution faults

Room #3

- 2 pcs FP2000 Fire Alarm Panels

- Total Loops: 13 pcs

- Total Faults: 94 pcs

- 6th FAP: 36 pcs communication faults, 19 pcs bypass faults

- 7th FAP: 30 pcs communication faults, 9 pcs bypass faults

Room #4

- 4 pcs FP2000 Fire Alarm Panels

- Total Loops: 30 pcs

- Total Faults: 104 pcs

- 8th FAP: No faults

- 9th FAP: 32 pcs communication faults, 15 pcs bypass faults, 9 pcs new devices

- 10th FAP: No faults

- 11th FAP: 3pcs communication faults, 10 pcs bypass faults, 35 pcs new devices

Room #5

- 2 pcs FP2000 Fire Alarm Panels

- Total Loops: 6 pcs

- Total Faults: 9 pcs

- 12th FAP: 3 pcs communication faults, 6 bypass faults

- QUALIFICATIONS AND PROPOSAL SUBMISSION REQUIREMENTS

Interested companies must demonstrate:

- Proven Experience in fire alarm system installation and upgrades

- Successful completion of similar projects

- Valid insurance and licenses

Proposal must include:

- Company profile including history, qualifications and experience

- List of key personnel who will be involved in the project, including their qualifications and experience

- References from similar projects

- Proof of insurance and relevant licenses

- WARRANTY AND COMMERCIAL TERMS

A minimum warranty period of 2 years is required, which includes site visits diagnosis of malfunctions and rectification of problems within 24 hours

Commercial Terms:

- Contractor’s All risk insurance: Project cost amount

- Third-Pary liability: 50% of project cost

- Advance Payment: 50% is available upon bank guarantee until the project completion date

- Retention: 5% for one year

- No interim Payments

- SELECTION CRITERIA

Proposals will be evaluated based on the following criteria:

- Compliance with the submission requirements

- Experience and qualifications of the company and key personnels

- Cost-effectiveness of the proposal

- Warranty period

- Duration of works and readiness to start it immediately

- References and past performance on similar projects

- SUBMISSION DEADLINE AND CONTACT INFORMATION

Proposals Must be submitted by September 4, 2024, to the following Address:

Beka Tsiklauri
Procurement Manager
E-Mail: b.tsiklauri@tbilisimall.com
Mobile: +995 591 51 43 09

Thank you for your interest in this project. We look forward to receiving your proposal.