## Лист1
Thickener area
| INSTRUMENT_TAG | PLC_TAG | DESCRIPTION | SIGNAL_TYPE |  | RANGE | POWER_SUPPLY
| ZF01-LT-200 |  | Final Tailings Sump Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-205 |  | Tailings Flow From Floatation | AI | 4-20 mA | 0 - 1500 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Tailings Flow From Floatation (Totalizer) | DI | RIO is active | 1 pulse - 0.3 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-DT-206 |  | Tailings Density | AI | 4-20 mA | 800 - 2000 kg/m3 | 24VDC | ACTIVE | 2-wire connection
| ST02-LT-210 |  | Thickener Feed Distribution Tank Level | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-DT-221 |  | Thickener TH-001 Underflow Density | AI | 4-20 mA | 800 - 2000 kg/m3 | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-222 |  | Thickener TH-001 Underflow Flow | AI | 4-20 mA | 0 - 500 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Thickener TH-001 Underflow Totalizer | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-LT-230 |  | ST02-TK003 Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-DT-231 |  | Thickener TH-002 Underflow Density | AI | 4-20 mA | 800 - 2000 kg/m3 | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-232 |  | Thickener TH-002 Underflow Flow | AI | 4-20 mA | 0 - 500 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Thickener TH-002 Underflow Totalizer | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-LT-240 |  | Overflow Holding Tank Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-PT-245 |  | Overflow Holding Tank Water Distribution Pressure Control | AI | 4-20 mA | 0 - 20 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-246 |  | Water Flow to Basin from Overflow Holding Tank | AI | 4-20 mA | 0 - 1200 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow to Basin from Overflow Holding Tank (Totalizer) | DI | RIO is active | 1 pulse - 0.5 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-FT-247 |  | Water Distribution Flow to Thickeners | AI | 4-20 mA | 0 - 500 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Distribution Flow to Thickeners (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-FT-248 |  | Water Flow to ST02-TK003 for dilution | AI | 4-20 mA | 0 - 200 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow to ST02-TK003 for dilution (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-PT-250 |  | Water Pressure from Basin | AI | 4-20 mA | 0 - 16 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-252 |  | Water Flow from Basin | AI | 4-20 mA | 0 - 200 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow from Basin (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-QT-257 |  | Overflow Holding Tank PH Control | AI | 4-20 mA | 0 - 14 | 24VDC | ACTIVE | 2-wire connection
| ST02-LT-270 |  | Gland Seal Holding Tank ST02-TK004 Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-271 |  | Water Flow to ST02-TK004 | AI | 4-20 mA | 0 - 60 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow to ST02-TK004 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-LT-272 |  | Sump Tank BA-001 Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-LT-273 |  | Sump Tank BA-003 Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ZF01-PS-275 |  | Gland Seal Flow to ZF01-PU-005 | DI | RIO is active |  | 24VDC | ACTIVE | 3-wire connection (power supply + PNP switch)
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ZF01-PS-276 |  | Gland Seal Flow to ZF01-PU-006 | DI | RIO is active |  | 24VDC | ACTIVE | 3-wire connection (power supply + PNP switch)
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-FT-279 |  | Gland Seal Water Distribution Flow | AI | 4-20 mA | 0 - 60 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Gland Seal Water Distribution Flow (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-PT-280 |  | Gland Seal Water Distribution Pressure Control | AI | 4-20 mA | 0 - 50 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-FT-285 |  | Gland Seal Water Flow to ST02-PU-020/ST02-PU-024 | AI | 4-20 mA | 0 - 30 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active)
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-FT-293 |  | Gland Seal Water Flow to Underflow and Overflow Pumps | AI | 4-20 mA | 0 - 30 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active)
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-FIT-407 |  | Tailings Main Line 1 Flow to Filtration Area | AI | 4-20 mA | 0 - 500 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Tailings Main Line 1 Flow to Filtration Area (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-DIT-409 |  | Tailings Main Line 1 Flow Density Control | AI | 4-20 mA | 800 - 2000 kg/m3 | 24VDC | ACTIVE | 2-wire connection
| ST02-PIT-410 |  | Tailings Main Line 1 Pressure | AI | 4-20 mA | 0 - 16 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-FIT-424 |  | Tailings Main Line 2 Flow to Filtration Area | AI | 4-20 mA | 0 - 500 m3/hr | 24VDC | ACTIVE | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Tailings Main Line 2 Flow to Filtration Area (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC | ACTIVE
[5 empty] | 24 V DC power supply |  | 24VDC | ACTIVE
| ST02-LT-240.1 |  | Transit Overflow Holding Tank ST02-ТК-002.1 Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | 2-wire connection
| ST02-DIT-426 |  | Tailings Main Line 2 Flow Density Control | AI | 4-20 mA | 800 - 2000 kg/m3 | 24VDC | ACTIVE | 2-wire connection
| ST02-PIT-427 |  | Tailings Main Line 2 Pressure | AI | 4-20 mA | 0 - 16 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-PIT-280.1 |  | Gland Seal Pressure Control for ST02-PU-020/ST02-PU-024 | AI | 4-20 mA | 0 - 20 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-PIT-280.2 |  | Gland Seal Pressure Control for Underflow and Overflow Pumps | AI | 4-20 mA | 0 - 20 bar | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-020-TT1 |  | ST02-PU-020 Internal Bearing Temperature | AI | 4-20 mA | 0 - 100 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-020-TT2 |  | ST02-PU-020 External Bearing Temperature | AI | 4-20 mA | 0 - 100 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-020-TT3A |  | ST02-PU-020 A-Winding Temperature | AI | 4-20 mA | 0 - 200 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-020-TT3B |  | ST02-PU-020 B-Winding Temperature | AI | 4-20 mA | 0 - 200 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-020-TT3C |  | ST02-PU-020 C-Winding Temperature | AI | 4-20 mA | 0 - 200 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-021-TT1 |  | ST02-PU-021 Internal Bearing Temperature | AI | 4-20 mA | 0 - 100 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-021-TT2 |  | ST02-PU-021 External Bearing Temperature | AI | 4-20 mA | 0 - 100 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-021-TT3A |  | ST02-PU-021 A-Winding Temperature | AI | 4-20 mA | 0 - 200 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-021-TT3B |  | ST02-PU-021 B-Winding Temperature | AI | 4-20 mA | 0 - 200 C | 24VDC | ACTIVE | 2-wire connection
| ST02-PU-021-TT3C |  | ST02-PU-021 C-Winding Temperature | AI | 4-20 mA | 0 - 200 C | 24VDC | ACTIVE | 2-wire connection
| FCV-248 |  | Tailings Main Line Density Control Valve (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | Tailings Main Line Density Control Valve (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| HCV-254 |  | ST02-ТК-002 Feeding Line From Basin (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | ST02-ТК-002 Feeding Line From Basin (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| HS-286 |  | Gland Seal Pressure Control for ST02-PU-020/ST02-PU-024 (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | Gland Seal Pressure Control for ST02-PU-020/ST02-PU-024 (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| HS-294 |  | Gland Seal Pressure Control for Underflow and Overflow Pumps (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | Gland Seal Pressure Control for Underflow and Overflow Pumps (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| HCV-253 |  | Water Distribution to Thickeners, Reserve Line, (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | Water Distribution to Thickeners, Reserve Line, (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| HCV-249 |  | Water Flow Control for Thickener's sprayers (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | Water Flow Control for Thickener's sprayers (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| LCV-240 |  | ST02-ТК-002 Level Control (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | ST02-ТК-002 Level Control (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| LCV-270 |  | ST02-ТК-004 Level Control (Feedback) | AI | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Feedback | pneumatic regulating actuator 24VDC 4-20 mA control signal, 4-20 mA positioner (feedback)
|  |  | ST02-ТК-004 Level Control (Set Point) | AO | 4-20 mA | 0 - 100 % | 24VDC | ACTIVE | Set point
| HS-219.1 |  | TH-001 Water Cleaner Feed Line (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | TH-001 Water Cleaner Feed Line (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | TH-001 Water Cleaner Feed Line (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | TH-001 Water Cleaner Feed Line (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-220.1 |  | TH-002 Water Cleaner Feed Line (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | TH-002 Water Cleaner Feed Line (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | TH-002 Water Cleaner Feed Line (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | TH-002 Water Cleaner Feed Line (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-417 |  | ST02-PU-024 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-024 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-024 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-024 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-428 |  | ST02-PU-024 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-024 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-024 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-024 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-243.1 |  | ST02-PU-004.1 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-004.1 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-004.1 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-004.1 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-244.1 |  | ST02-PU-004.1 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-004.1 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-004.1 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-004.1 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-242.1 |  | ST02-PU-003.1 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-003.1 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-003.1 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-003.1 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-241.1 |  | ST02-PU-003.1 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-003.1 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-003.1 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-003.1 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-411 |  | ST02-PU-020 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-020 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-020 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-020 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-400 |  | ST02-PU-020 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-020 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-020 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-020 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-239.1 |  | Thickener TH-002 Underflow Feed Line (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | Thickener TH-002 Underflow Feed Line (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-002 Underflow Feed Line (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | Thickener TH-002 Underflow Feed Line (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-230.1 |  | Thickener TH-001 Underflow Feed Line (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | Thickener TH-001 Underflow Feed Line (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-001 Underflow Feed Line (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | Thickener TH-001 Underflow Feed Line (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-228 |  | ST02-PU-029 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-029 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-029 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-029 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-227 |  | ST02-PU-028 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-028 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-028 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-028 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-237 |  | ST02-PU-030 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-030 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-030 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-030 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-238 |  | ST02-PU-031 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-031 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-031 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-031 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-230 |  | ST02-PU-029 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-029 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-029 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-029 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-229 |  | ST02-PU-028 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-028 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-028 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-028 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-240 |  | ST02-PU-031 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-031 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-031 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-031 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-239 |  | ST02-PU-030 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-030 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-030 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-030 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-301 |  | Thickener TH-002 Slurry Recirculation Velve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | Thickener TH-002 Slurry Recirculation Velve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-002 Slurry Recirculation Velve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | Thickener TH-002 Slurry Recirculation Velve (Opened Status) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-302 |  | Thickener TH-001 Slurry Recirculation Velve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | Thickener TH-001 Slurry Recirculation Velve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-001 Slurry Recirculation Velve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | Thickener TH-001 Slurry Recirculation Velve (Opened Status) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-234.1 |  | ST02-PU-031 Flushing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-031 Flushing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-031 Flushing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HCV-234 |  | ST02-PU-030 Flushing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-030 Flushing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-030 Flushing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HCV-235 |  | Thickener TH-002 Underflow Feed Line Flushing valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-002 Underflow Feed Line Flushing valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-002 Underflow Feed Line Flushing valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HCV-224.1 |  | ST02-PU-029 Flushing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-029 Flushing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-029 Flushing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HCV-224 |  | ST02-PU-028 Flushing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-028 Flushing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-028 Flushing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HCV-225 |  | Thickener TH-001 Underflow Feed Line Flushing valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-001 Underflow Feed Line Flushing valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-001 Underflow Feed Line Flushing valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-281 |  | ST02-PU-005 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-005 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-005 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-283 |  | ST02-PU-006 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-006 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-006 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-284 |  | ST02-PU-006 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-006 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-006 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-282 |  | ST02-PU-005 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | ST02-PU-005 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-005 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-219 |  | Thickener TH-001 Water Spray Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-001 Water Spray Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-001 Water Spray (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-220 |  | Thickener TH-002 Water Spray Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | закрыта | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-002 Water Spray Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | открыта
|  |  | Thickener TH-002 Water Spray (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | открыть (1-открыть, 0-закрыть)
| HS-241 |  | ST02-PU-003 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-003 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-003 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-003 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-242 |  | ST02-PU-029 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-029 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-029 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-029 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-243 |  | ST02-PU-004 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-004 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-004 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-004 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-244 |  | ST02-PU-029 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-029 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-029 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-029 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-214 |  | Thickener TH-001 Flocculant Dosing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-001 Flocculant Dosing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-001 Flocculant Dosing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-216 |  | Thickener TH-002 Flocculant Dosing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-002 Flocculant Dosing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-002 Flocculant Dosing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-213 |  | Thickener TH-001 Flocculant Dosing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-001 Flocculant Dosing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-001 Flocculant Dosing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-215 |  | Thickener TH-002 Flocculant Dosing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Thickener TH-002 Flocculant Dosing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Thickener TH-002 Flocculant Dosing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-251 |  | Basin Line Water Shut Off Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Basin Line Water Shut Off Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Basin Line Water Shut Off Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-256 |  | Tailings Main Line 2 Flushing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Tailings Main Line 2 Flushing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Tailings Main Line 2 Flushing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-255 |  | Tailings Main Line 1 Flushing Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 1-coil Solenoid
|  |  | Tailings Main Line 1 Flushing Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | Tailings Main Line 1 Flushing Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open (1 - open, 0 - close)
| HS-201 |  | ST02-PU-005 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-005 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-005 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-005 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-202 |  | ST02-PU-005 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-005 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-005 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-005 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-203 |  | ST02-PU-006 Inlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-006 Inlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-006 Inlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-006 Inlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-204 |  | ST02-PU-006 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-006 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-006 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-006 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS-305.2 |  | ST02-PU-008 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-008 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-008 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-008 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Open
| HS305.1 |  | ST02-PU-007 Outlet Valve (Closed Status) | DI |  |  | 24VDC | ACTIVE | Closed | Pneumatic actuator, 2-coils Solenoid
|  |  | ST02-PU-007 Outlet Valve (Opened Status) | DI |  |  | 24VDC | ACTIVE | Opened
|  |  | ST02-PU-007 Outlet Valve (Close Command) | DO | + 24 V from module |  | 24VDC | ACTIVE | Close
|  |  | ST02-PU-007 Outlet Valve (Open Command) | DO | + 24 V from module |  | 24VDC |  | Open