Technical specifications for the purchase of equipment

Robot station for preparation and dosing of flocculant

Tbilisi 2024

- Robot station for preparation and dosing of flocculant

  - Purpose of the device

# The device is designed to automatically prepare and dose flocculant solution.

  - Types/sizes and capacities of flocculant preparation stations

| 1 | Required flocculant (mixture) capacity, m3/h | 0,1 – 0,3 |
| --- | --- | --- |
| 2 | concentration, % | От 0,05 |
| 3 | interval of concentrations of the working solution, % | 0,05-1,0 |
| 4 | Mass concentration, kg/m3 | 10 |
| 5 | Equipment material | stainless steelAISI 304 |
| 6 | Working mode | throughout the year, 24/7 |
| 7 | Enlisting | - Automation of dosing and dilution systems; - Availability of HMI for process control and management; - Availability of station operation in automatic, manual control, as well as remote automatic modes; - Ability to display the following information indicators at the top level: – waste tank level; – operating statuses of pumps/mixers – rotation of pumps/mixers; - Rotation of pumps/mixers must be controlled using 4-20 mA analog signals, digital channels are not allowed; - protection of automation from power supply voltage surges; - ABB ACS880 should be used as a variable frequency drive (VFD); - From transfusion; - Regulating the supply of flocculant working cost. |
| 8 | Power supply: voltage, V / frequency Hz | 400/50 |
| 9 | Degree of protection | IP65 |

# 1.3. Compilation of goods

| number | name | Amount, unit |
| --- | --- | --- |
| 1 | Robot station for preparation and dosing of flocculant | 2 ც. |
| 2 | A set of spare parts for equipment (SPTA) for a service life of 24 months. | 1 ც. |

# 3. Basic technical and technological requirements for material and technical resources

3.1. The design and material characteristics of parts and systems must be suitable for the climatic conditions and allow for rapid installation of wearing parts at the station installation site.

3.2. Base units and assemblies must operate on all-season hydraulic and transmission lubricants and oils.

3.3. The guaranteed service life of the electric motor and gearbox must be at least 10,000 hours.

3.4. Presentation of guaranteed service life of the main units and components of the station.

- Requirements for electrical equipment

Cable and wire products must be flexible (with multi-core conductors), with non-flammable insulation that does not lose its plasticity at temperatures from +40 to -20℃.

- Warranty period conditions

The warranty period is 12 months from the date of completion of acceptance tests or 24 months from the date of delivery to the Customer's warehouse. In the event of suspension of operation due to the fault of the Supplier, the warranty period is extended for the period of delay.

- List of required documentation

The Supplier shall provide the Customer with technical documentation:

| № | Documentation | Date of submission** |
| --- | --- | --- |
| 1 | Dimensional drawing | 10 days after signing the agreement |
| 2 | Operation, technical service instruction | Together with the device |
| 3 | Spare parts catalogue (electronic version) | Together with the device |
| 4 | Drawings of short-life details | Together with the device |
| 5 | Device passport | 10 days after signing the agreement |
| 6 | electrical schemes | Together with the device |
| 7 | Certificates of conformity, origin | Together with the device |

** Drawings must be submitted electronically in PDF and DWG format

Documentation shall be provided in English, Russian languages.

- Packaging requirements

It is not regulated.

- Additional terms

Not applicable.

- Attracting sub-suppliers

It is allowed by agreement with the Customer.

- Terms of delivery

The product must be delivered under the following conditions: DDP urban-type settlement Kazreti station, Georgia, or FCA.