## Sheet1
Technical data sheet for low voltage busduct
General
1.1 | Project Name: | Tailings facility, filtration unit
1.2 | Country of destination: | Georgia
1.3 | Main specification Doc. No.: | Electrical room general arrangement
1.4 | Related list of attachment | Electrical room general arrangement; SLD filtration unit
INDIVIDUAL SITE CONDITIONS
2.1 | Altitude | < 100m above mean sea level
2.2 | Erection | indoor ventilated
2.3 | Design air temperature (Indoor) | Max. 35 °C / Min. 0 °C
2.4 | Relative Humidity (Indoor) | Max 80 % / Min. 50 %
2.5 | Atmosphere (Indoor) | Ventilated (Pressurized) Electrical Equipment Room
2.6 | Snow load | Not Applicable
2.7 | Wind load | Not Applicable
2.8 | Sand load | Not Applicable
2.9 | Earthquake load | zone 1 (grade 9)
POWER SUPPLY AND DISTRIBUTION SYSTEM FOR BUS DUCT SERVICE
3.1 | System rated voltage (no-load voltage) | 380 V
3.2 | Service voltage | 380 V
3.3 | Static voltage variation | ±5%
3.4 | Dynamic voltage variation | ±10%
3.5 | Rated frequency | 50 Hz
3.6 | Frequency variation | ± 0.4 Hz (Dynamic) / ± 0.2 Hz (Static)
3.7 | Combination of voltage and frequency variation | Within limits for Zone – A of. IEC 60034-1
3.8 | Number of phases | 3AC + PE
3.9 | N conductor | Required
3.10 | System neutral | solidly grounded
3.11 | Rated short-time withstand current | 43 kA rms
3.12 | Rated duration of short circuit | 1 s
3.13 | Rated peak withstand current | 90 kA (to be discussed)
3.14 | Power frequency test voltage (rms) | 3 kV 1 min
BUS DUCT BASIC DATA
4.1 | Number of bus duct systems | 2
4.2 | Bus duct tag numbers | to be discussed
4.3 | Bus duct path from / to | as per Electrical room general arrangement and SLD filtration unit
4.4 | Manufacturer | to be filled by Vendor
4.5 | Model number | to be filled by Vendor
4.6 | Model type | non-segregated
4.7 | Conductor material | High Conductivity Copper
4.8 | Conductor insulation material | Epoxy resin coating
4.9 | Isolator material | as per Vendor standart
4.10 | Enclosure material, if any | Sheet Steel, 2mm thick
4.11 | IP Protection class | IP 55
4.12 | Painting, if any | as per Vendor standart
BUS DUCT TECHNICAL DATA
5.1 | Rated current | 4000A
5.2 | Waste heat of bus duct (full load) | ......kW/m (to be filled by Vendor)
5.3 | Impedance AC resistance @ 75°C / 50 Hz average reactance | ...... micro ohm/m (to be filled by Vendor) ...... micro ohm/m (to be filled by Vendor)
5.4 | Voltage drop due to inductivity (at full load; for LV application) | …… V/m (to be filled by Vendor)
5.5 | Cross-section area of conductor phase/neutral | …… mm² / …… mm² (to be filled by Vendor)
5.6 | Total weight | to be filled by Vendor
5.7 | Total dimension length x width x height | …… x …… x …… mm (to be filled by Vendor)
5.8 | Wall and floor penetrations applicable | Applicable
5.9 | Supporting structures material corrosion protection | to be filled by Vendor
5.10 | Special Tools, if any | to be filled by Vendor
5.11 | Spare Parts | to be filled by Vendor