## Sheet1
Technical data sheet for dry type transformer (filtration)
INDIVIDUAL SITE CONDITIONS
1.1 | Project Name: | Tailings facility, filtration unit
1.2 | Country of destination: | Georgia
1.3 | Main specification Doc. No.: | DISTRIBUTION TRANSFORMERS SPECIFICATION
1.4 | Related list of attachment | FILTRATION MAIN EL.EQUIPMENT GENERAL ARRANGEMENT; SLD filtration unit; Transformer technical data
1.5 | Atmosphere | Indoor
1.6 | Installation | Indoor
1.7 | Design air temperature indoor | Max. 55 °C, min. -10 °C
1.8 | Inside Design Relative Humidity | to be discussed later
1.9 | Altitude above mean sea level | < 1000 m
1.10 | Seismic Load | level 9
1.11 | Snow load | Not applicable
1.12 | Wind load | Not applicable
1.13 | Sand load | Not applicable
INDIVIDUAL POWER SUPPLY AND DISTRIBUTION SYSTEM
2.1 | Tag No. | to be discussed later
2.2 | System rated voltage (no-load voltage) | 400V (secondary side)
2.3 | Service voltage | 400V, 3AC + PEN
2.4 | Static voltage variation | ±5%
2.5 | Dynamic voltage variation | ±10%
2.6 | Harmonic content on primary side | class 1 according EN 61000-2-4
2.7 | Harmonic content on secondary side | class 2 according EN 61000-2-4
2.8 | Rated frequency | 50 Hz
2.9 | Static frequency variation | ± 0.2 %
2.10 | Dynamic frequency variation | ± 0.4 %
2.11 | Combination of voltage and frequency variation | Within limits for Zone – A of IEC 60034-1
2.12 | Short-circuit current on primary side (including plant contribution) | 65 kA for 1 sec
2.13 | Short-circuit current on secondary side (including plant contribution) | 65 kA for 1 sec
2.14 | Factor for peak current | 2.5
2.15 | System neutral | Solidly grounded
TRANSFORMER
3.1 | Number of pieces | 2
3.2 | Manufacturer | Hittachi
3.3 | Type / Number | as per Vendor
3.4 | Transformer typeTransformer type | Dry type distribution transformer
3.5 | Rated voltage Ur | Primary 6 kV, secondary 0.4 kV
3.6 | Vector group | Dyn 11
3.7 | Rated frequency fr | 50 Hz
3.8 | Duty | Continuous
3.9 | No. of windings | Two
3.10 | Rated current Ir | Primary 240,5 A, secondary as per SLD filtration unit
3.11 | Rated power Sr | 2500kVA
3.12 | Impedance voltage uKr | 6.5 % without negative tolerance
3.13 | Cooling | AN (AF)
3.14 | No load current I0 | as per Vendor A prim. at 100% Voltage & as per Vendor A prim. at 110% Voltage
3.15 | No load losses P0 | as per Vendor kW at 100% Voltage & as per Vendor kW at 110% Voltage
3.16 | Full load losses Pfl | as per Vendor kW
3.17 | Short circuit losses Pkr | as per Vendor kW
3.18 | Reactance at rated current & frequency | as per Vendor
3.19 | Resistance voltage drop uR cos φ = 1 cos φ = 0,8 | as per Vendor % as per Vendor %
3.20 | X1 / R1 - ratio | as per Vendor
3.21 | X0 / R0 - ratio | as per Vendor
3.22 | Zero Sequence Impedance Z0 | as per Vendor
3.23 | Efficiency ƞ at cos φ = 1 and 4 / 4 load 3 / 4 load 2 / 4 load cos φ = 0,8 and 4 / 4 load 3 / 4 load 2 / 4 load | as per Vendor
3.24 | Maximum Efficiency ƞ max | (at 40 % load)
3.25 | Magnitude of Inrush current & duration | 62,5kA 1 sec
3.26 | Short-circuit duration for design | 2 sec
3.27 | Insulation class | F
3.28 | Corrosion class | C5I
3.29 | Fire class | F1
3.30 | Operating mode | DB
3.31 | Pre-load and additional load at motor start | as per Vendor
3.32 | Temperature rise of windings | as per Vendor K (max. 100 K)
3.33 | Thermal time constant | as per Vendor min
3.34 | Thermal withstand | as per Vendor x Ir / sec
3.35 | Mechanical short circuit withstand | as per Vendor kA prim.
3.36 | Rated Insulation Voltage | 12 kV primary 1.1 kV sec
3.37 | Dielectric Test Voltage | 28 kV primary 3 kV sec
3.38 | Rated Impulse Withstand Voltage | 60 kV primary
3.39 | MV / LV phase sequence | L1 L2 L3 / To suit switchgear (TPN)
3.40 | Heat to be dissipated | as per Vendor kW
3.41 | Sound pressure level in 1 m distance | 65dB(A) (max. 65 dB(A))
3.42 | Dimensions L x W x H | as per FILTRATION MAIN EL.EQUIPMENT GENERAL ARRANGEMENT
3.43 | Weight Core & winding weight total weight max. shipping weight weight of removable parts | as per Vendor
3.44 | Erection | On rails with flat wheels
3.45 | Installation | On wheels with locking system
3.46 | Type of enclosure | Min. IP 31 & main terminal box min. IP 55
3.47 | Painting | RAL 7035
3.48 | Tagging & Lettering | Stainless steel rating-plate placed on the long side, indelibly engraved with data like Item Number and Service Title as well as prescribed by IEC 60726
3.49 | Accessories | Lifting lugs for complete transformer and accessories Vibration Isolation Frame Temperature Control relay for alarm / trip and remote indication on LV switchgear / DCS. Neutral CTs
OFF-LOAD TAPS
4.1 | Mounting | On primary & operable from ground level
4.2 | Lettering | Every position of the taps
4.3 | Steps | -5,0 % / -2,5 % / 0 / +2,5 % / +5,0 % ( = 5 steps on Primary Side )
POWER CONNECTION
5.1 | Primary side | Cable from bottom of transformer front Connection screwed
5.2 | Secondary side | Bus bar from top Bus bar flange opposite to MV side Connection screwed Bus bar size - to be discussed
5.3 | Star point | Bus Duct
5.4 | Accessories | Isolated cable shield busbar
ADDITIONAL TERMINAL BOX
6.1 | Control voltage for signals | 220 V AC, isolated for protection relay
6.2 | Protection class | Min. IP 55
6.3 | Accessories | cable glands earthed PE busbar isolated cable shield busbar earthed cable armour clamp
MEASURING AND PROTECTION DEVICES
9.1 | Temperature (number, type, place, function, lettering) | per phase 1 x resistance thermometer double PT100 (3-wire-system from terminal box) per phase 2 x PTC; all three phases shall be in series for alarm at 110 °C and trip at 120 °C. Signals to the relay on the transformer or directly to the protection relay to be discussed later
INCOMING SWITCHING DEVICE
10.1 | Nominal voltage | 6kV
10.2 | Nominal current | the same as primary coil if the transformer
10.3 | Design of the device | The load switch must be attached to the transformer casing and have common MV busbars
10.4 | Interlocks
10.4.1 |  | - Reverse Transformation Exclusion
10.4.2 |  | - Blocking the grounding blades when the disconnector is on
10.4.3 |  | - interlocking the opening of the compartment doors when the voltage is on
10.5 | Grounding switch | YES, on the incoming cables side
10.6 | Protection class | IP 42
TYPE TEST CERTIFICATES
10.1 | Temperature test | Yes / No Certificate No.
10.2 | Impulse test | Yes / No Certificate No.
SPECIAL TEST CERTIFICATES
11.1 | Short Circuit test | Yes / No Certificate No.