## Sheet1
Technical data sheet for low voltage MCC
General
1.1 | Project Name: | Tailings facility, filtration unit
1.2 | Country of destination: | Georgia
1.3 | Main specification Doc. No.: | MCC specification
1.4 | Related list of attachment | Typical MCC diagrams; MCC filtration general view; SLD filtration unit; Consumer list filtration unit; FILTRATION MAIN EL.EQUIPMENT GENERAL ARRANGEMENT; MCC reactive power compensation unit
1.5 | Switchgear Type | as per vendor standard
1.6 | Communication protocol | Ethernet IP for DCS, IEC 61850
1.7 | Communication interface | RS485
1.8 | Signal exchange described in | to be added later
INDIVIDUAL SITE CONDITIONS
2.1 | Individual site conditions | -
2.2 | Location Type | indoor
2.3 | Climatic condition - indoor | 3K3 (Based on IEC 60721, no solar radiation)
2.4 | Special climatic conditions | no solar radiation (indoor application)
2.5 | Classification of biological conditions | 3B2
2.6 | Classification of chemically active substances | 3C2 / no salt mist
2.7 | Classification of mechanical conditions | 3M1
2.8 | Pollution (IEC 61439) | pollution degree 3 (industrial)
2.9 | Altitude | < 1000m
2.10 | EMC environment | Environment A
2.11 | EMC compatibility level acc to. IEC 61000-2-4 | class 3
2.12 | Seismic zone | level 9
ELECTRICAL RATING OF SWITCHGEAR
3.1 | Type of neutral earthing | TN-C (to be discussed)
3.2 | System Nominal voltage (V) | 380 V
3.3 | Static voltage variation | ±5%
3.4 | Instantaneous voltage variation | ±10%
3.5 | Rated insulation voltage (Ui) | 1000 V
3.6 | Overvoltage Category | IV
3.7 | Dielectric test voltage | 3.5 kV
3.8 | Impulse withstand voltage | 8 kV
3.9 | Rated frequency (fr) | 50 Hz
3.10 | Frequency variation | +/- 0.2 Hz (Normal) / +/- 0.4 Hz (Maximum)
3.11 | Altitude correction to be considered | NO
3.12 | Rated current (InA) (Incomer & Busbar) | 4000 A
3.13 | Rated diversity factor (assembly) | 1.0
3.14 | Power factor | compensated
3.15 | Rated current (Inc) for (Feeders) | as per SLD filtration unit
3.16 | Rated diversity factor (vertical sections) | 0.8
3.17 | Prospective short-circuit current at supply terminals Icp (kA) | 43 kA
3.18 | Duration of Icp (tcp) | 1 sec
3.19 | Short circuit protective device (SCPD) to be included in the incoming unit & bus ties of the assembly | YES
3.20 | Arc fault compliance to IEC 61641 | YES
3.21 | Arc fault current and duration | 1 sec
3.22 | Data associated with loads likely to contribute to short circuit current | as per SLD filtration unit
3.23 | Rated voltage and frequency for (control and protection) | 220V/24V DC protection; 220V AC control
3.24 | Control voltage individually protected by MCB | per bus section
3.25 | Auxiliary supply voltage:
| - Space heater and panel illumination | 220V AC
| - Contactors | 220V AC
| - MCU / Soft Starter / VSD control supply | 220V/24V DC, redundant (grounded minus) from AC UPS supply (at one point for each bus section)
| - ACB spring charging, closing and tripping indication, Numerical relays | 220 V DC, +/-/PE (grounded) (at one point for each bus section)
3.26 | Signal interface with DCS | as per mapping list (to be discussed)
3.27 | Signal interface with Package Unit PLC | as per mapping list (to be discussed)
MECHANICAL DATA OF SWITCHGEAR AND GENERAL DESIGN
4.1 | Number of cubicles | as per Consumer list filtration unit/SLD filtration unit
4.2 | Manufacturer | as per Vendor
4.3 | Type / Number | as per Vendor
4.4 | Dimension of Switchgear: Width Depth Height | as per MCC filtration general view/FILTRATION MAIN EL.EQUIPMENT GENERAL ARRANGEMENT
4.5 | Weight per cubicle / total | as per Vendor
4.6 | Waste heat per cubicle / total | as per Vendor
4.7 | Installation method | floor standing / double front
4.8 | Room floor design | concrete floor
4.9 | Protection class (IP coding) | IP 42 (closed doors), IP 20 (open doors)
4.10 | Painting | RAL 7035
4.11 | Cabinet lights and convenience outlets | as per vendor standard
4.12 | Cabinet space heaters | YES in cable connection compartments
4.13 | Options: | Insulated busbars
Operating arrangements
4.14 | Access to manually operated devices | authorized person
4.15 | Location of manually operated devices | Easily accessible
4.16 | Isolation of load installation equipment items | to be discussed
INCOMER
5.1 | Number of feeders | 2
5.2 | Lettering | to be discussed
5.3 | Form of internal separation IEC 61439-2 Table 104 | Form 3b
5.4 | Dimension of Cubicle: Width Depth Height | as per MCC filtration general view/FILTRATION MAIN EL.EQUIPMENT GENERAL ARRANGEMENT
5.5 | Weight per cubicle | as per Vendor
5.6 | Power connection type / location | busduct frombottom
5.7 | Power connection conductor mat. | copper
5.8 | Power connection quantity and size: | Directly horizontal busbar connection
5.9 | Degree of Protection for bus ducts | IP55
5.10 | Air break type circuit breaker Make: Type: Rating: | 4000 A
5.11 | Method of functional unit connection | W = withdrawable
5.12 | CB No. of poles | 4
5.13 | Earthing facility inside of cable connection compartment | YES
5.14 | Current transformers: measuring core 3 x 4000/1 A protection core 3 x 4000/1 A (Pfc only Phase L2) 1 x 4000/5 A | 5 VA, 0.5 FS 5 5 VA, 5P 20 50 VA, 1 FS 5
5.15 | Rated voltage and frequency for control and protection | 220 V DC +/-/PE (grounded)
5.16 | Push buttons and selector switches | ☒ON; ☒OFF; ☒Lamp Test
5.17 | Indication Lamps / LED's | ☒ON; ☒OFF; ☒Alarm; ☒Ready; ☒Trip; ☒Trip from upstream
5.18 | Measuring & Protection for protection, monitoring, metering and control | YES
5.19 | Instruments accuracy | class 0.2s
5.20 | Separate mimic diagram on front of the switchgear required | YES
5.21 | Analogue instruments | Voltmeter with selector switch
5.22 | Additional instruments | Power meter
BUS TIE
6.1 | Number of feeders | 1
6.1 | Lettering | to be discussed
6.1 | Form of internal separation IEC 61439-2 Table 104 | Form 3b
6.1 | Dimension of Cubicle: Width Depth Height | as per MCC filtration general view/FILTRATION MAIN EL.EQUIPMENT GENERAL ARRANGEMENT
6.1 | Power connection type / location | as per vendor standard
6.1 | Air break type circuit breaker Make: Type: Rating: | 4000 A
6.1 | Method of functional unit connection | W = withdrawable
6.1 | CB No. of poles | 4 pole
6.1 | Current transformers: measuring core 3 x 4000/1 A protection core 3 x 4000/1 A for overcurrent | 5 VA, 0.5 FS 5 5 VA, 5P 20
6.1 | Rated voltage and frequency for control and protection | 220 V DC +/-/PE (grounded)
6.1 | Push buttons and selector switches | ☒ON; ☒OFF; ☒AUTO-MANUAL; ☒Lamp Test ☒Isolation Incomer A; ☒Isolation Incomer B; ☒Isolation Bus Coupler
6.1 | Indication Lamps / LED's | ☒ON; ☒OFF; ☒Alarm; ☒Ready; ☒Trip
6.1 | Analogue instruments | Voltmeter with selector switch
6.1 | Measuring & Protection for protection, monitoring, metering and control | YES
6.1 | Separate mimic diagram on front of the switchgear required | YES
6.1 | Automatic Transfer System (ATS) Make: Type: | YES by protrection relay (or plc)
MOTOR – FEEDER
7.1 | Number of feeders | as per Typical MCC diagrams/SLD filtration unit
7.2 | Applicable for | Motor Starters (FVNR / FVR,softstarter,VSD)
7.3 | Applicable Typical Wiring diagrams | YES
7.4 | Method of functional unit connection | W = withdrawable
7.5 | Form of internal separation IEC 61439-2 Table 104 | Form 3b
7.6 | Power connection type / location | cables from top
7.7 | Power connection conductor mat. | copper
7.8 | Cable reduction factor for connection terminal co-ordination | 0.4
7.9 | Switching device | as per typical wiring diagrams
7.10 | Periodic duty | Class 3 (up to three operating cycles per hour)
7.11 | Control voltage | 24 V DC, redundant (grounded minus) from AC UPS supply (at one point for each bus section)
7.12 | Control Interface | MCU bus interface
7.13 | Local control station interface | YES
7.14 | Hardwired Interface to ESD or SIS | YES
7.15 | Automatic reacceleration | to be discussed
7.16 | Status indication | ☒RUN; ☒OFF; ☒Ready; ☒Fault
7.17 | Type of equipment | VFD - ABB ACS880; DOL - Siemens simocode pro
7.18 | Measurement device | as per vendor standard
HEATER – FEEDER
8.1 | Number of feeders | as per Typical MCC diagrams/SLD filtration unit
8.2 | Applicable for | as per Typical MCC diagrams/SLD filtration unit
8.3 | Applicable Typical Wiring diagrams | yes
8.4 | Method of functional unit connection | W = withdrawable
8.5 | Form of internal separation IEC 61439-2 Table 104 | Form 3b
8.6 | Power connection type / location | cables from top
8.7 | Power connection conductor mat. | copper
8.8 | Cable reduction factor for connection terminal co-ordination | 0.4
8.9 | Switching device | as per typical wiring diagrams
8.10 | Periodic duty | as per vendor standard
8.11 | Control voltage | 24 V DC, redundant (grounded minus) from AC UPS supply (at one point for each bus section)
8.12 | Control Interface | MCU bus interface
8.13 | Local control interface | YES
8.14 | Hardwired Interface to ESD or SIS | YES
8.15 | Automatic reacceleration | to be discussed
8.16 | Status indication | ☒ON; ☒OFF; ☒Ready; ☒Fault
8.17 | Type of equipment | VFD - ABB ACS880; DOL - Siemens simocode pro
8.18 | Measurement device | as per vendor standard
POWER FEEDER – SUB FEEDER
9.1 | Number of feeders | as per Typical MCC diagrams/SLD filtration unit
9.2 | Applicable for | Power Feeders (FU, PUE, PUS)
9.3 | Applicable Typical Wiring diagrams | yes
9.4 | Method of functional unit connection | W = withdrawable
9.5 | Form of internal separation IEC 61439-2 Table 104 | Form 3b
9.6 | Power connection type / location | cables from top
9.7 | Power connection conductor mat. | copper
9.8 | Cable reduction factor for connection terminal co-ordination | 0.4
9.9 | Switching device | as per typical wiring diagrams
9.10 | Periodic duty | Not applicable
9.11 | Control voltage | 24 V DC, redundant (grounded minus) from AC UPS supply (at one point for each bus section)
9.12 | Control Interface | conventional hardwired
9.13 | Local control interface | NO
9.14 | Hardwired Interface to ESD or SIS | YES
9.15 | Automatic reacceleration | Not applicable
9.16 | Status indication | ☒Ready; ☒Fault
9.17 | Measurement device | as per vendor standard
POWER FACTOR CORRECTION CAPACITORS
10.1 | Number of feeders | as per MCC reactive power compensation unit
10.2 | Method of functional unit connection | separate column
10.3 | Switching device | ABB
10.4 | Local control interface | YES
10.5 | Applicable equipment:
10.6 | - capacitors | Any applicable
10.7 | - control | ABB
10.8 | Reactivwe power for compensation | 338,89kVAr