| Technical Assignment Vibration and Temperature monitoring systems selection for pump-units | Abstract Vibration and Temperature monitoring systems for P/S “Bagebi” pump-units. |
| --- | --- |

Table of Contents

1. Project Overview	2

2.   Introduction	2

3.   Scope of Supply	2

4.   Technical Requirements	4

Appendix: Existing pump data.	4

# Project Overview

-   Project Name: Vibration and Temperature monitoring systems for P/S “Bagebi” pump-units.

-   Location: P/S “Bagebi”.

-   Number of pump-units: 5 pieces.

-   Client/Owner: GWP

-   Date: 1/Apr./2025

# 2.   Introduction

This document outlines the requirements for the purchase and delivery of pump and motor bearing temperature and vibration monitoring systems for pumping station “Bagebi”. These systems are crucial for proactive maintenance, ensuring the reliability and longevity of our pumping equipment, and preventing costly downtime.

Objective:

- To acquire reliable and accurate pump-unit bearing temperature and vibration monitoring systems.

- To enable continuous monitoring of critical pump components.

- To implement a predictive maintenance strategy based on real-time data.

- To reduce maintenance costs and improve operational efficiency.

- To enhance the safety of personnel and equipment.

# Important Note 1: Please pay attention to the fact that Temperature and Vibration should be monitored on motor as well.

# 3.   Scope of Supply

Complete pump bearing temperature monitoring systems, including:

- Temperature sensors suitable for pump bearing applications.

- Signal conditioners and transmitters.

- Data acquisition units.

- Cabling and connectors.

- Software for data visualization and analysis.

Complete pump bearing vibration monitoring systems, including:

- Vibration sensors suitable for pump bearing applications.

- Signal conditioners and transmitters.

- Data acquisition units.

- Cabling and connectors.

- Software for data visualization and analysis.

Important Note 2: drilling of the pump body is prohibited for the installation of sensors. Alternative ways should be proposed by the supplier.

Integration capabilities:

- Systems should be capable of integrating with existing plant SCADA or DCS systems.

- Provide clear communication protocol documentation.

Installation and commissioning support:

- Supervision of installation.

- Commissioning and testing of the systems.

- Training for plant personnel on system operation and maintenance.

Documentation:

- Detailed technical specifications.

- Installation and operation manuals.

- Maintenance procedures.

- Calibration certificates.

# 4.   Technical Requirements

Temperature Monitoring:

- Measurement range: from 0°C to +120°C or from 0°C to 150°C.

- Accuracy: ± 1%.

- Response time: 1 sec.

Vibration Monitoring:

- Measurement range: 0-25 mm/s RMS.

- Working range: from 0°C to +120°C or from 0°C to 150°C.

- Accuracy: ± 1%.

Important Note 3: Please note that the measuring equipment can have temperature range either from 0°C to +120°C or from 0°C to +150°C.

Data Acquisition:

- Data storage capacity: For 1 month data.

- Real-time data display.

- Alarm and notification capabilities.

Software:

- User-friendly interface.

- Trend analysis and reporting.

- Alarm management.

- Data export capabilities.

# Appendix 1: Existing pump-unit data.

Bagebi pump-unit data.pdf

# Appendix 2: Schematic Drawing of Bagebi Pumping Station with Marking of Ethernet connection and pumps that need monitoring system.

Drawing of Bagebi Pumping Station with Indications.png

# Appendix 3: Schematic Drawing of Bagebi Pumping Station without Marker – PDF Format.

Drawing of Bagebi Pumping Station without Markers.pdf