## Sheet1
From | TR1
MDB1 | INComing A | 1600 |  |  | 12 | 1 | 240
Power Connection Number | Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
CompDB1 | 67 | 1 | 160 | 380 | E1.1-0 | 5 | 50 | N2XH
1 | 9 | 1 | 25 | 380 | E1.1-1 | 5 | 4 | N2XH
2 | 5 | 1 | 16 | 380 | E1.1-2 | 5 | 2.5 | N2XH
3 | 18 | 1 | 40 | 380 | E1.1-3 | 5 | 10 | N2XH
4 | 18 | 1 | 40 | 380 | E1.1-4 | 5 | 10 | N2XH
5 | 12 | 1 | 25 | 380 | E1.1-5 | 5 | 4 | N2XH
6 | 12 | 1 | 25 | 380 | E1.1-6 | 5 | 4 | N2XH |  | „
7 | 15 | 1 | 32 | 380 | E1.1-7 | 5 | 6 | N2XH
8 | 0.5 | 1 | 16 | 220 | E1.1-8 | 3 | 2.5 | N2XH
Laminator1 | 148 | 1 | 320 | 380 | E1.1-9 | 5 | 150 | N2XH
Laminator2 | 148 | 1 | 320 | 380 | E1.1-10 | 5 | 150 | N2XH
Laminator3 | 148 | 1 | 320 | 380 | E1.1-11 | 5 | 150 | N2XH
9 | 15 | 1 | 32 | 380 | E1.1-12 | 5 | 6 | N2XH
10 | 9 | 1 | 25 | 380 | E1.1-13 | 5 | 4 | N2XH
14 | 5 | 1 | 16 | 380 | E1.1-14 | 5 | 2.5 | N2XH
15 | 6 | 1 | 16 | 380 | E1.1-15 | 5 | 2.5 | N2XH
16 | 5 | 1 | 16 | 380 | E1.1-16 | 5 | 2.5 | N2XH
17 | 2 | 1 | 16 | 220 | E1.1-17 | 3 | 2.5 | N2XH
18 | 8 | 1 | 25 | 380 | E1.1-18 | 5 | 4 | N2XH
19 | 2 | 1 | 16 | 220 | E1.1-19 | 3 | 2.5 | N2XH
20 | 1 | 1 | 40 | 220 | E1.1-20 | 3 | 6 | N2XH
21 | 5 | 1 | 16 | 380 | E1.1-21 | 5 | 2.5 | N2XH
22 | 5 | 1 | 16 | 380 | E1.1-22 | 5 | 2.5 | N2XH
23 | 6 | 1 | 16 | 380 | E1.1-23 | 5 | 2.5 | N2XH
24 | 5 | 1 | 16 | 380 | E1.1-24 | 5 | 2.5 | N2XH
Charging Room | 5 | 1 | 25 | 220 | E1.1-25 | 3 | 4 | N2XH
Air Fan | 10 | 1 | 25 | 380 | E1.1-26 | 5 | 4 | N2XH
LDP1 | 35 |  |  | 380 | E1.1-27 | 5 |  | N2XH
jami | 724.5
From | MDB1
LDB1 | INComing A |  | 320 | 380 |  | 5 | 150 | N2XH
| Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
[8 empty] | N2XH | 1
[8 empty] | N2XH | 2
[8 empty] | N2XH | 3
[8 empty] | N2XH | 4
[8 empty] | N2XH | 5
[8 empty] | N2XH | 6
[8 empty] | N2XH | 7
[8 empty] | N2XH | 8
[8 empty] | N2XH | 9
[8 empty] | N2XH | 10
[8 empty] | N2XH | 11
[8 empty] | N2XH | 12
[8 empty] | N2XH | 13
[8 empty] | N2XH | 14
[8 empty] | N2XH | 15
[8 empty] | N2XH | 16
[8 empty] | N2XH | 17
[8 empty] | N2XH | 18
[8 empty] | N2XH | 19
[8 empty] | N2XH | 20
[8 empty] | N2XH | 21
[8 empty] | N2XH | 22
[8 empty] | N2XH | 23
[8 empty] | N2XH | 24
[8 empty] | N2XH | 25
[8 empty] | N2XH | 26
[8 empty] | N2XH | 27
jami | 0
From | TR2
MDB2 | INComing A | 1600 |  |  | 12 | 1 | 240
Connection Number | Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
CompDB2 | 67 | 1 | 160 | 380 |  | 5 | 50 | N2XH
1 | 9 | 1 | 25 | 380 | E2.1-1 | 5 | 4 | N2XH
2 | 5 | 1 | 16 | 380 | E2.1-2 | 5 | 2.5 | N2XH
3 | 15 | 1 | 32 | 380 | E2.1-3 | 5 | 6 | N2XH
4 | 5 | 1 | 16 | 380 | E2.1-4 | 5 | 2.5 | N2XH
5 | 5 | 1 | 16 | 380 | E2.1-5 | 5 | 2.5 | N2XH
6 | 6 | 1 | 16 | 380 | E2.1-6 | 5 | 2.5 | N2XH | 7
7 | 15 | 1 | 32 | 380 | E2.1-7 | 5 | 6 | N2XH | 8
8 | 9 | 1 | 25 | 380 | E2.1-8 | 5 | 4 | N2XH | 9
9 | 10 | 1 | 25 | 380 | E2.1-9 | 5 | 4 | N2XH | 10
10 | 5 | 1 | 16 | 380 | E2.1-10 | 5 | 2.5 | N2XH | 11
11 | 6 | 1 | 16 | 380 | E2.1-11 | 5 | 2.5 | N2XH | 12
12 | 5 | 1 | 16 | 380 | E2.1-12 | 5 | 2.5 | N2XH | 13
13 | 8 | 1 | 25 | 380 | E2.1-13 | 5 | 4 | N2XH | 14
14 | 2 | 1 | 16 | 220 | E2.1-14 | 3 | 2.5 | N2XH | 15
15 | 5 | 1 | 16 | 380 | E2.1-15 | 5 | 2.5 | N2XH
Laminator1 | 148 | 1 | 320 | 380 | E2.1-16 | 5 | 150 | N2XH
Laminator2 | 148 | 1 | 320 | 380 | E2.1-17 | 5 | 150 | N2XH
Laminator3 | 148 | 1 | 320 | 380 | E2.1-18 | 5 | 150 | N2XH
16 | 18 | 1 | 40 | 380 | E2.1-19 | 5 | 10 | N2XH
17 | 18 | 1 | 40 | 380 | E2.1-20 | 5 | 10 | N2XH
18 | 12 | 1 | 32 | 380 | E2.1-21 | 5 | 6 | N2XH | 22
19 | 12 | 1 | 32 | 380 | E2.1-22 | 5 | 6 | N2XH
20 | 0.5 | 1 | 16 | 220 | E2.1-23 | 3 | 2.5 | N2XH | 24
21 | 1.8 | 1 | 16 | 220 | E2.1-24 | 3 | 2.5 | N2XH | 25
22 | 1.2 | 1 | 16 | 220 | E2.1-25 | 3 | 2.5 | N2XH | 26
23 | 1 | 1 | 40 | 220 | E1.1-26 | 3 | 6 | N2XH
Detail 1-(1-3) | 15 | 1 | 63 | 380 | D2.1-1 | 5 | 10 | N2XH
Detail 1-(3-6) | 15 | 1 | 63 | 380 | D2.1-2 | 5 | 10 | N2XH
Detail 1-(6-9) | 15 | 1 | 63 | 380 | D2.1-3 | 5 | 10 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S2.1-1 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S2.1-2 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-3 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-4 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-5 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-6 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-7 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-8 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-9 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-10 | 3 | 2.5 | N2XH
Sockets Group | 3 | 1 | 20 | 220 | S1.1-11 | 3 | 2.5 | N2XH
jami | 763.5
From | MDB1
CompDP1 | INComing A | 1 | 160 |  |  | 5 | 50
| Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
Compressor1 | 65 | 1 | 125 | 380 | C1.1-1 | 5 | 35 | N2XH
Cad 200-1 | 2 | 1 | 16 | 220 | C1-1-2 | 3 | 1.5 | N2XH
jami | 67
From | MDB2
CompDP2 | INComing A | 1 | 160 |  |  | 5 | 50
MCB Title | Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
Compressor2 | 65 |  | 125 | 380 | C2.1-1 | 5 | 35 | N2XH
Cad 200-2 | 2 |  | 16 | 220 | C2.1-2 | 3 | 1.5 | N2XH
jami | 67
From | TR3
MDB3 | INComing A |  | 400 | 380 | 1 | 1 | 240 | N2XH
MCB Title | Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
OfficeDP | 35 | 1 | 80 | 380 | E3.1-1 | 5 | 25 | N2XH
MechDP | 150 | 1 | 350 | 380 | E3.1-2 | 5 | 150 | N2XH
Server | 10 | 1 | 63 | 220 | E3.1-3 | 3 | 10 | N2XH
jami | 195
From | MDB3
Office DP | INComing A |  | 80 | 380 |  | 5 | 25 | N2XH
MCB Title | Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
Sockets Group | 3 | 1 | 16 | 220 | S1.1-1 | 3 | 2.5 | N2XH | 1
Sockets Group | 3 | 1 | 16 | 220 | S1.1-2 | 3 | 2.5 | N2XH | 2
Sockets Group | 3 | 1 | 16 | 220 | S1.1-3 | 3 | 2.5 | N2XH | 3
Sockets Group | 3 | 1 | 16 | 220 | S1.1-4 | 3 | 2.5 | N2XH | 4
Sockets Group | 3 | 1 | 16 | 220 | S1.1-5 | 3 | 2.5 | N2XH | 5
Sockets Group | 3 | 1 | 16 | 220 | S1.1-6 | 3 | 2.5 | N2XH | 6
Sockets Group | 3 | 1 | 16 | 220 | S1.1-7 | 3 | 2.5 | N2XH | 7
Sockets Group | 3 | 1 | 16 | 220 | S1.1-8 | 3 | 2.5 | N2XH | 8
Sockets Group | 3 | 1 | 16 | 220 | S1.1-9 | 3 | 2.5 | N2XH | 9
Sockets Group | 3 | 1 | 16 | 220 | S1.1-10 | 3 | 2.5 | N2XH | 10
Sockets Group | 3 | 1 | 16 | 220 | S1.1-11 | 3 | 2.5 | N2XH | 11
Sockets Group | 3 | 1 | 16 | 220 | S1.1-12 | 3 | 2.5 | N2XH | 12
Sockets Group | 3 | 1 | 16 | 220 | S1.1-13 | 3 | 2.5 | N2XH | 13
Sockets Group | 3 | 1 | 16 | 220 | S1.1-14 | 3 | 2.5 | N2XH | 14
Sockets Group | 3 | 1 | 16 | 220 | S1.1-15 | 3 | 2.5 | N2XH | 15
Sockets Group | 3 | 1 | 16 | 220 | S1.1-16 | 3 | 2.5 | N2XH | 16
Lightnings group | 0.78 | 1 | 16 | 220 | L2-1 | 3 | 1.5 | N2XH | 17
Lightnings group | 0.78 | 1 | 16 | 220 | L2-2 | 3 | 1.5 | N2XH | 18
Lightnings group | 0.78 | 1 | 16 | 220 | L2-3 | 3 | 1.5 | N2XH | 19
Lightnings group | 0.78 | 1 | 16 | 220 | L2-4 | 3 | 1.5 | N2XH | 20
Lightnings group | 0.78 | 1 | 16 | 220 | L2-5 | 3 | 1.5 | N2XH | 21
jami | 51.9
From | MDB3
MechDB | INComing A |  | 320 | 380 |  | 5 | 150 | N2XH
| Power KW | QUANT | MCB A | Voltage V | Wire number | Wire Core | Wire Size mm2 | Wire Size mm2
Pumps | 1.6 | 1 | 16 | 220 | M1.1-1 | 3 | 1.5 | N2XH | 1
Boiler Room | 1 | 1 | 16 | 220 | M1.1-2 | 3 | 1.5 | N2XH | 2
Fan | 0.5 | 1 | 16 | 220 | M1.1-3 | 3 | 1.5 | N2XH | 3
Chiller1 | 50 | 1 | 125 | 380 | M1.1-4 | 5 | 35 | N2XH | 4
Chiller2 | 50 | 1 | 125 | 380 | M1.1-5 | 5 | 35 | N2XH | 5
AHU1 | 12 | 1 | 50 | 380 | M1.1-6 | 5 | 6 | N2XH | 6
AHU2 | 12 | 1 | 50 | 380 | M1.1-7 | 5 | 6 | N2XH | 7
AHU3 | 2.5 | 1 | 16 | 380 | M1.1-8 | 5 | 1.5 | N2XH | 8
AHU4 | 2.5 | 1 | 16 | 380 | M1.1-9 | 5 | 1.5 | N2XH | 9
AHU5 | 0.5 | 1 | 16 | 380 | M1.1-10 | 5 | 1.5 | N2XH | 10
El.Calorifer | 4 | 1 | 25 | 220 | M1.1-11 | 3 | 4 | N2XH | 11
Multi Split | 8 | 1 | 32 | 380 | M1.1-12 | 5 | 4 | N2XH | 12
Multi Split | 8 | 1 | 32 | 380 | M1.1-13 | 5 | 4 | N2XH | 13
Multi Split | 8 | 1 | 32 | 380 | M1.1-14 | 5 | 4 | N2XH | 14
Multi Split | 7 | 1 | 32 | 380 | M1.1-15 | 5 | 4 | N2XH | 15
Multi Split | 7 | 1 | 32 | 380 | M1.1-16 | 5 | 4 | N2XH | 16
Multi Split | 7 | 1 | 32 | 380 | M1.1-17 | 5 | 4 | N2XH | 17
Multi Split | 7 | 1 | 32 | 380 | M1.1-18 | 5 | 4 | N2XH | 18
Multi Split | 7 | 1 | 32 | 380 | M1.1-19 | 5 | 4 | N2XH | 19
Split | 3 | 1 | 16 | 380 | M1.1-20 | 5 | 1.5 | N2XH | 20
Split | 3 | 1 | 16 | 380 | M1.1-21 | 5 | 1.5 | N2XH | 21
Split | 2 | 1 | 16 | 380 | M1.1-22 | 5 | 1.5 | N2XH | 22
Split | 2 | 1 | 16 | 380 | M1.1-23 | 5 | 1.5 | N2XH | 23
Water Pump1 | 4 | 1 | 20 | 380 | M1.1-24 | 5 | 1.5 | N2XH | 24
Water Pump2 Reserve | 0 | 1 | 20 | 380 | M1.1-25 | 5 | 1.5 | N2XH | 25
Drenage Pump1 | 1 | 1 | 16 | 380 | M1.1-26 | 5 | 1.5 | N2XH | 26
Drenage Pump2 Reserve | 0 | 1 | 16 | 380 | M1.1-27 | 5 | 1.5 | N2XH | 27
jami | 210.6