APPROVED

(Position, name, surname, date)

# RECORDING LOG OF THE SYSTEM TECHNICAL MAINTENANCE AND

# REPAIR WORKS

Fire detection and emergency alarm

(fire fighting system type)

Ownership, name and address of the site

Kind, type and commissioning date

Performer of the system's technical maintenance

(name, registration number of the company, name, surname and phone number of the servicing person)

Staff on duty:

Responsible for the system operation:

Terms for the technical servicing and maintenance of the system developed in accordance with

EN -54-14

(name, number and issuing date of the law or regulation and documentation developed by the manufacturer of the system devices)

| No. | Name of the work | Frequency of works | Responsible person for the site or for the system maintenance (indicate a person who is responsible for the work performance in a specific period of time) |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| 1 | Fire alarm control panel. |  |  |

| 1.1 | External check of panel. Check of light indication elements in standby mode. Check of date and time indication conformity, adjustment, if necessary (2) | Monthly | Responsible for operation: |
| --- | --- | --- | --- |
| 1.2 | Check the condition of the panel – whether the panel shows stationary state, whether all deviations from the stationary state have been registered in the log and information thereof based on established procedure has been provided to the technical maintenance organization (1) (2) | Daily | Staff on duty at the site |
| 1.3 | Check – whether sufficient attention has been paid to all emergency events registered since the previous business day (2) | Daily | Staff on duty at the site |
| 1.4 | Check whether the system operation is sufficiently restored after the damage, inspection or stopping, if necessary. (2) | Daily | Staff on duty at the site |
| 1.5 | From each loop or area turn on at least one detector (manual button) for checking the emergency alarm signal. (100% of the total volume per year) (2) (3) | Monthly |  |
| 1.6 | Checking of the system connection with other fire-protective equipment (1) (3) | Quarterly | Responsible for operation: |
| 1.7 | Check of the power supply switching from the main supply to reserve supply and back. (2) (3) | Quarterly | Responsible for operation: |
| 1.8 | Unblocking check of the emergency evacuation doors (1) (2) | Quarterly | Responsible for operation: |
| 1.9 | Check of the ventilation disconnection (1) (2) | Quarterly | Responsible for operation: |
| 1.10 | Check of the spare parts (modules, button glass, detectors) and document availability (instructions, plans, zone plans, technical projects, log of activation events and damages, acceptance deeds, correctness of the indicated phone numbers, etc.) (1) (2) (3) | Quarterly | Responsible for operation: |

| 1.11 | Visual check, tightening of contacts, check of grounding. Visual check to confirm that all cable connections and equipment are safe, undamaged and accordingly protected (1) (2) (3) | Annually | Responsible for operation: |
| --- | --- | --- | --- |
| 1.12 | Check of remaining capacity of the accumulator (2) (3) | Annually | Responsible for operation: |
| 1.13 | Check on any changes to premises, visual check of the detector working area (1) (2) | Annually | Responsible for operation: |
| 1.14 | Reserve copying of the panel data (3) | After any changes, if no changes – annually, the data carrier must be replaced in 5 years | Responsible for operation: |
| 1.15 | User briefing (1) (2) (3) | Whenever necessary | Responsible for operation: |
| 1.16 | Software check up. Creation of backup copy. | Annually | Responsible for operation: |
| 1.17 | Written confirmation that all established system deficiencies are made known to the responsible person (2) | Quarterly | Work performer, Responsible for operation: |
| 2 | Detectors and manual buttons |  |  |
| 2.1 | Cleaning of transducers from dirt and dust (2) (3) (4) | Whenever necessary and upon panel readings | Responsible for operation: |
| 2.2 | Check in alarm mode (100% of the total volume per year). All detectors and buttons must be checked during the year. (2) (3) (4) | Monthly | Responsible for operation: |

| 2.3 | Check by disconnecting detector from the loop and causing short circuit to loop, the signal of damage must appear on the panel. 100% of detectors must be checked within 5 years. 20% during the year or 5% quarterly from the total amount. (3) | Quarterly | Responsible for operation: |
| --- | --- | --- | --- |
| 2.4 | Check whether detectors are located in right places and are not visually damaged. At least 0.5 m of free space shall be around the detectors. (1) (2) (3) | Annually | Responsible for operation: |
| 2.5 | Detectors, for which the sensitivity level has reached the threshold and calibration is required, shall be sent to factory or replaced. (1) (3) (4) | Whenever necessary and upon panel readings | Responsible for operation: |
| 2.6 | Check for any changes to the structure of the building and number of occupants that could affect the conditions for the placement of manual alarm transducers, detectors and sound devices, by performing visual inspection in such situation (1) (2) (3) | Quarterly | Responsible for operation: |
| 3 | Fire alarm sound signalling devices and control modules |  |  |
| 3.1 | Check of the signal/alarm working capacity (2) (3) | Quarterly | Responsible for operation: |
| 3.2 | Check of the third systems connected to modules (turning on the voice announcement, disconnection of ventilation, elevator operation, unblocking of evacuation doors) (1) (2) (3) | Quarterly | Responsible for operation: |
| 3.3 | Check of all control modules. 25% of the total number quarterly (3) | Quarterly | Responsible for operation: |
| 3.4 | Check the ability of the control and alarm equipment to operate all door blocking and opening functions. (1) (2) | Quarterly | Responsible for operation: |
| 3.5 | Check of the signal transmission between the buildings (2) | Quarterly | Responsible for operation: |

APPROVED

(position, name, surname, date)

Annex 9C to the Cabinet Regulations

No. 238

of 19 April 2016

# RECORDING LOG OF THE SYSTEM TECHNICAL MAINTENANCE AND

# REPAIR WORKS

Voice announcement system

(fire fighting system type)

Ownership, name and address of the site

System kind, type and

commissioning date

Performer of the system's technical maintenance

(name, registration number of the company, name, surname and phone number of the servicing person)

Staff on duty:

Terms for the technical servicing and maintenance of the system developed in accordance with

EN-54

(name, number and issuing date of the law or regulation and documentation developed by the manufacturer of the system devices)

| No. | Name of the work | Frequency of the works | Responsible person for the site or for the system maintenance (indicate a person who is responsible for the work performance in a specific period of time) |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| 1 | Voice announcing system (Public Address) |  |  |
| 1.1 | External check of the controller. Check of light indication elements in standby mode. (2) | Monthly | Responsible for operation: |

| 1.2 | Check of the controller condition – whether the indication shows stationary state, whether all deviations from the stationary state have been registered in the log and information thereof based on established procedure has been provided to the technical maintenance organization (1) | Daily | Site staff |
| --- | --- | --- | --- |
| 1.3 | Check – whether sufficient attention has been paid to all damage events registered since the previous business day (3) | Daily | Site staff |
| 1.4 | Perform functional check by turning on system in automatic mode, manual mode (2) (3) | Monthly | Responsible for operation: |
| 1.5 | Check of the power supply switching from the main supply to reserve supply and back. (2) (3) | Quarterly | Responsible for operation: |
| 1.6 | Check of availability of the original spare parts and documentation (orders, plans, premises and area lists, technical projects, activation and damage event log, deeds of delivery and acceptance, correctness of indicated phone numbers etc.) (1) (2) (3) | Quarterly | Responsible for operation: |
| 1.7 | Visual check, tightening of contacts, check of grounding. Visual check to confirm that all cable connections and equipment are safe, undamaged and accordingly protected (1) (2) (3) | Semi-annually | Responsible for operation: |
| 1.8 | Loudness sufficiency check. Not less than 65 dB in each room. (2) (3) | Annually | Responsible for operation: |
| 1.9 | User briefing (1) (2) (3) | Whenever necessary | Responsible for operation: |
| 1.10 | Check of the system compatibility documentation. (2) (3) | Annually | Responsible for operation: |

APPROVED

(position, name, surname, date)

# RECORDING LOG OF THE SYSTEM TECHNICAL MAINTENANCE AND

# REPAIR WORKS

Smoke extraction system with hatches

(fire fighting system type)

Ownership, name and address of the site

Kind, type, name and

commissioning date

of the system

Performer of the system's technical maintenance

(name, registration number of the company, name, surname and phone number of the servicing person)

Staff on duty:

Terms for the technical servicing and maintenance of the system developed in accordance with

(name, number and issuing date of the law or regulation and documentation developed by the manufacturer of the system devices)

| No. | Name of the work | Frequency of the works | Responsible person for the site or for the system maintenance (indicate a person who is responsible for the work performance in a specific period of time) |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| 1 | Smoke extraction system panel |  |  |
| 1.1. | External check of panel. Check of light indication elements in standby mode. (2) | Monthly | Responsible for operation: |

| 1.2 | Check the condition of the panel – whether the indication show stationary state, or whether all deviations from the stationary state have been registered in the log and information thereof based on established procedure has been provided to the technical maintenance organization (1) | Daily | Site staff |
| --- | --- | --- | --- |
| 1.3 | Check – whether sufficient attention has been paid to all emergency events registered since the previous business day (3) | Daily | Site staff |
| 1.4 | Check whether the system operation is sufficiently restored after the damage, inspection or stopping, if necessary. (3) | Daily | Site staff |
| 1.5 | Perform functional check by turning on system. One check must take place in winter pATSod between November 1 and March 1. (1) (2) (3) | Quarterly | Responsible for operation: |
| 1.6 | Checking of the system connection with other fire-protective equipment (1) (3) | Quarterly | Responsible for operation: |
| 1.7 | Check of the power supply switching from the main supply to reserve supply and back. (2) (3) | Quarterly | Responsible for operation: |
| 1.8 | Check of the spare parts (modules, button glass, detectors) and document availability (instruction, plans, room and area lists, technical projects, log of activation events and damages, acceptance deeds, of the indicated phone numbers etc.) (1) (2) (3) | Quarterly | Responsible for operation: |
| 1.9 | Visual check, tightening of contacts, check of grounding. Visual check to confirm that all cable connections and equipment are safe, undamaged and accordingly protected (1) (2) (3) | Semi-annually | Responsible for operation: |
| 1.10 | User briefing (1) (2) (3) | Whenever necessary | Responsible for operation: |

| 1.11 | Preparation of the system for winter period. Lubrication of hinges, treatment of sealant rubber. (1) (2) (3) | Annually | Responsible for operation: |
| --- | --- | --- | --- |
| 1.12 | Check of the system compatibility documentation. | Annually | Responsible for operation: |

APPROVED

(position, name, surname, date)

# RECORDING LOG OF THE SYSTEM TECHNICAL MAINTENANCE AND

# REPAIR WORKS

Fire fighting water supply system

(fire fighting system type)

Ownership, name and address of the site

Kind, type and

commissioning date

Performer of the system's technical maintenance

(name, registration number of the company, name, surname and phone number of the servicing person)

Staff on duty:

Terms for the technical servicing and maintenance of the system developed in accordance with

EN-54

(name, number and issuing date of the law or regulation and documentation developed by the manufacturer of the system devices)

| No. | Name of the work | Frequency of the works | Responsible person for the site or for the system maintenance (indicate a person who is responsible for the work performance in a specific period of time) |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| 1 | Fire fighting and water supply system |  |  |
| 1 | Fire fighting pumps with electric engine, direction valves |  |  |

| 1.1 | Inspection and external cleaning when necessary and check of condition of the shut-off valve | Quarterly | Responsible for operation: |
| --- | --- | --- | --- |
| 1.2 | Tightening of fastenings when necessary, check of protective grounding, inspection of cable routes | Quarterly | Responsible for operation: |
| 1.3 | Automatic pump turn-on test: reduce water pressure in the start device, thus simulating condition of automatic start; | Quarterly | Responsible for operation: |
| 1.4 | Check the turn-on pressure once the pump powered on | Quarterly | Responsible for operation: |
|  | Automatic pump flow test: |  |  |
| 1.5 | During operation at full load, check each water supply pump in installation (via test line connection, which is connected to the pump supply pipe, down the stream from the pump outflow counter-running valve) and the same pressure/flow readings, as written on the plate of its characteristics, must be received. Specific pressure loss is acceptable in the supply pipeline and valves between the source and each control unit | Annually | Responsible for operation: |
| 2 | Sprinklers, temperature-sensitive valves and sprayers |  |  |
| 2.1 | Check of sprinklers, temperature-sensitive valves and sprayers (replace painted and deformed sprinklers, temperature-sensitive valves and sprayers) | Annually | Responsible for operation: |
| 3 | Pipelines and pipeline supports |  |  |
| 3.1 | Fix the materials wrapped around the pipes if needed | Quarterly | Responsible for operation: |
| 3.2 | Check for anti-corrosion presence on the pipelines and their brackets | Annually | Responsible for operation: |

| 3.3 | Check if pipelines are not used as electric grounding. Sprinkler pipelines may not be used for the grounding of electric equipment. Remove any electric equipment grounding from them and install any other types of grounding | Annually | Responsible for operation: |
| --- | --- | --- | --- |
| 4 | Electricity supply |  |  |
| 4.1 | Check if any secondary power supply sources operate with sufficient power (diesel generator, reserve inlet) | Annually | Responsible for operation: |
| 5 | Shut-off valves |  |  |
| 5.1 | Check the correctness of the position of all main signal valves | Monthly | Responsible for operation: |
| 5.2 | All shut-off valves controlling water flow to sprinklers must be run, to make sure that they operate well and correctly. The number of to-be-checked shut-off valves includes also all water supply check valves and emergency valves, as well as any other area or additional shut-off valves | Annually | Responsible for operation: |
| 6 | Visual inspection of the electromagnetic bolt |  |  |
| 6.1 | External inspection of the bolt. The bolts must be shut and set in an automatic mode. Check of the sealant validity for operation and presence of inscriptions. | Monthly | Responsible for operation: |
| 7. | Flow relays |  |  |
| 7.1 | Check if the flow relays operate correctly | Annually | Responsible for operation: |
| 7.2 | Manometer verification | Annually | Responsible for operation: |

| 8 | Fire fighting unit and remote central emergency board |  |  |
| --- | --- | --- | --- |
| 8.1 | Check the working capacity | Semi-annually | Responsible for operation: |
| 9 | Fire fighting taps (FT) cabinets |  |  |
| 9.1 | Check FT cabinet equipment (tap, hose, barrel, labels) | Quarterly | Responsible for operation: |
| 9.2 | Functional and mechanical check of FT | Annually | Responsible for operation: |
| 10 | Pump suction camera and rough purification filters |  |  |
| 10.1 | Rough purification filters of pump suction and operational camera and their protectors must be checked at least annually and cleaned when necessary | Annually | Responsible for operation: |
| 11 | Documentation |  |  |
| 11.1 | Check for presence of instructions for the staff on duty | Monthly | Responsible for operation: |
| 11.2 | Check for presence of the technological schemes | Monthly | Responsible for operation: |

NOTES:

  - All established defects must be recorded in the registration log, and any corrective actions taken as soon as possible!

  - Daily works should also be performed during performance of the monthly check! Monthly and daily works should also be performed during performance of the quarterly check! Quarterly, monthly and daily works should also be performed during performance of the annual check!