## Sheet1
LPG Mini filling station technical specifications
(5M3) LPG storage tank
Filling gas | [6 empty] | LPG (propane)
Design Specific Gravity | [6 empty] | 0.42 Kg/L
capacity | [6 empty] | 5M3
tank material | [6 empty] | Q345R
Tank body design thickness | [6 empty] | 8.53mm
End cover design thickness | [6 empty] | 8.51mm
design temperature | [6 empty] | 50 0C
working temperature | [6 empty] | -20~50 0C
Corrosion allowance | [6 empty] | 1.0 mm
design pressure | [6 empty] | 1.77MPa
Hydraulic test pressure | [6 empty] | 2.22 MPa
leak test pressure | [6 empty] | 1.77MPa
Heat treatment type | [6 empty] | Wholly get rid of tress
Main parts specification
Liquid level meter |  | Type |  |  |  | UZFAL-2.5FM
|  | Model |  |  |  | Magnetic level gauge
|  | Nominal pressure |  |  |  | PN2.5Mpa
|  | Surveying range |  |  |  | 50~2300mm
|  | Precision |  |  |  | 2.5Grade
Safe valve |  | Type |  |  |  | A42F-2.5-50
|  | Model |  |  |  | Inner full lift
|  | Nominal pressure |  |  |  | PN2.5 MPa
|  | Nominal diameter |  |  |  | DN50mm
|  | Opening pressure |  |  |  | 1.68-1.76MPa
|  | Closing pressure |  |  |  | 1.51~1.59MPa
|  | Complete opening pressure |  |  |  | <2.12 MPa
Loading and unloading device |  | Model |  |  |  | Quick tie-in
|  | Nominal Diameter |  | Inlet Gas phase |  | DN50mm
|  |  |  | Outlet gas phase |  | DN50mm
|  |  |  | Drain outlet phase |  | DN50mm
|  |  |  | Inlet Liquid phase |  | DN50mm
|  |  |  | outletLiquid phase |  | DN50mm
|  | Pressure meter |  |  |  | YN-100T
|  | Temperature gauge |  |  |  | WTQ-280
Cut-off valve |  | J41N-40 |  |  | Normal pressure | PN2.5 MPa
[5 empty] | Normal diameter | DN50MM
DN32MM
DN25MM
DN20MM
Safety valve of pipe |  | Type |  |  | A21F-25
|  | Normal pressure |  |  | PN2.5 MPa
|  | Normal diameter |  |  | DN15MM
Security reflux valve |  | Type |  |  | AH42F-25
|  | Normal pressure |  |  | PN2.5 MPa
|  | Normal diameter |  |  | DN25MM
Back pressure valve |  | Type |  |  | H42N-40
|  | Normal pressure |  |  | PN4MPa
|  | Normal diameter |  |  | DN50MM
Discharging pipe |  | Length |  |  | 4M
|  | Normal diameter |  |  | DN50/DN25MM
Shock-absorbing pipe |  | Length |  |  | 500MM
|  | Normal diameter |  |  | DN50MM
Flange |  | Normal pressure |  |  | PN2.5 MPa
|  | Normal diameter |  |  | DN65MM
DN50MM
DN32MM
DN25MM
DN15MM
Lpg gas pump(YQB15-5) | Flow (m³/h) |  |  | 15.5
| Inlet pressure (MPa) |  |  | ≤2.0
| outletpressure difference (Mpa |  |  | 0.5
| Pump rotate speed (r/min) |  |  | 780
| motor power |  |  | 5.5
(KW)
| Inlet aperture (mm) |  |  | 50
| Outlet aperture (mm) |  |  | 50
| Temperature rangeºC |  |  | -40~40
| Weight(kg) |  |  | 108
Explosive-proof motor | 7.5HP(5.5KW), Explosive Proof,
Dual Frequency 220V to 690V, 50Hz and 60Hz supplies applicable
LPG cylinder filling machine | Model |  | BSC-150
| Electricity voltage V |  | AC220
| Power(w) |  | 40
| Weighting scale |  | Can fill 0.5kg to 150kg LPG cylinde
| Measurement Precision |  | ±0.5%
| Rated Working Pressure |  | 1.6Mpa
| Temperature range ºC |  | -40~40
| Anti-explosion Rate |  | Exhibit II BT4