## Sheet1
| Description, Technical requirements. | Unit measure | QTY | Image
1 | LED emergency linear light fixture specs: 1) Plastic body, Color - White or Grey. 2) Min length 40cm. 3) Power Min - 6W, 4) Battery High Quality Li-IO, battery working time, on High level lighting - min 4 hours. On Low level lighting - min 7 hours. 5) Must be automatic "ON" when power goes out. 6) Must have a "TEST" button and indicator light Green/red shoving a battery charged. 7)IP-40, 8) 5000-5700K. Min 100Lm/W, ≥600Lm. 9) Warranty for light fixture 5 years and for battery 3 years | Pcs | 650